## Naini I
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet BOD (Design- <500 mg/l) | Final BOD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-06-01 | 81033 | 81.033 | 7.33 | 7.46 | 153 | 16 | 356 | 40 | 324 | 35 | NA | 700 | 0.3 | 24.5 | 1600000 | 1) Currently, reading of flow is taken from old flowmeter at Gaughat MPS as commissioning of flowmeter is not completed at Naini I STP. 2) Rehabilitation works for Gas Area of STP is in progress. 3) Rehabilitation work for Gaughat MPS & Chacharnalla SPS is in progress. 4) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 5) Checking of Calibration of flowmeter from OEM is required for both outlet of Gaughat MPS & inlet of Naini I STP as flow has rapidly increased from 50 - 60 MLD to 75 - 85 MLD from 07.05.2021.
2021-06-02 | 83220 | 83.22 | 7.39 | 7.51 | 159 | 18 | 360 | 36 | 328 | 33 | NA | 800 | 0.2 | 23.9 | 1300000
2021-06-03 | 84450 | 84.45 | 7.44 | 7.56 | 163 | 16 | 372 | 44 | 332 | 35 | NA | 700 | 0.1 | 22.4 | 1500000
2021-06-04 | 81710 | 81.71 | 7.48 | 7.66 | 160 | 19 | 356 | 40 | 328 | 33 | NA | 600 | 0.2 | 24.3 | 1200000
2021-06-05 | 80660 | 80.66 | 7.44 | 7.53 | 156 | 18 | 344 | 36 | 322 | 31 | NA | 700 | 0.3 | 24.5 | 1400000
2021-06-06 | 79090 | 79.09 | 7.49 | 7.51 | 159 | 16 | 352 | 44 | 326 | 35 | NA | 500 | 0.1 | 24.3 | 1500000
2021-06-07 | 86340 | 86.34 | 7.53 | 7.66 | 153 | 18 | 356 | 32 | 329 | 30 | NA | 600 | 0.2 | 24.2 | 1200000
2021-06-08 | 85780 | 85.78 | 7.44 | 7.56 | 149 | 16 | 360 | 40 | 327 | 34 | NA | 500 | 0.3 | 24.3 | 1400000
2021-06-09 | 59210 | 59.21 | 7.52 | 7.61 | 160 | 20 | 372 | 36 | 324 | 35 | NA | 700 | 0.2 | 24.1 | 1300000
2021-06-10 | 84340 | 84.34 | 7.46 | 7.58 | 156 | 22 | 356 | 40 | 328 | 30 | NA | 500 | 0.3 | 24.4 | 1500000
2021-06-11 | 76350 | 76.35 | 7.39 | 7.56 | 152 | 18 | 352 | 36 | 320 | 31 | NA | 800 | 0.2 | 24.5 | 1600000
2021-06-12 | 79070 | 79.07 | 7.47 | 7.61 | 156 | 19 | 364 | 40 | 328 | 33 | NA | 600 | 0.4 | 24 | 1400000
2021-06-13 | 95180 | 95.18 | 7.39 | 7.52 | 149 | 18 | 336 | 36 | 318 | 32 | NA | 500 | 0.3 | 24.1 | 1500000
2021-06-14 | 94190 | 94.19 | 7.53 | 7.66 | 153 | 20 | 348 | 40 | 322 | 34 | NA | 700 | 0.2 | 23.7 | 1400000
2021-06-15 | 77540 | 77.54 | 7.49 | 7.55 | 149 | 22 | 360 | 44 | 326 | 35 | NA | 600 | 0.2 | 24.3 | 1500000
2021-06-16 | 80120 | 80.12 | 7.51 | 7.6 | 152 | 24 | 372 | 36 | 301 | 30 | NA | 500 | 0.3 | 24.4 | 1600000
2021-06-17 | 77890 | 77.89 | 7.36 | 7.41 | 146 | 26 | 336 | 40 | 294 | 33 | NA | 800 | 0.3 | 24.5 | 1300000
2021-06-18 | 102360 | 102.36 | 7.44 | 7.49 | 138 | 22 | 344 | 32 | 288 | 30 | NA | 600 | 0.3 | 24.1 | 1500000
2021-06-19 | 97900 | 97.9 | 7.38 | 7.46 | 126 | 20 | 336 | 36 | 282 | 34 | NA | 500 | 0.2 | 24.4 | 1300000
2021-06-20 | 88620 | 88.62 | 7.52 | 7.58 | 152 | 21 | 348 | 40 | 306 | 35 | NA | 700 | 0.2 | 24 | 1200000
2021-06-21 | 73470 | 73.47 | 7.49 | 7.66 | 156 | 19 | 360 | 32 | 322 | 30 | NA | 600 | 0.3 | 24.3 | 1500000
2021-06-22 | 78270 | 78.27 | 7.56 | 7.64 | 160 | 20 | 336 | 36 | 319 | 33 | NA | 500 | 0.2 | 24.4 | 1300000
2021-06-23 | 85520 | 85.52 | 7.63 | 7.56 | 152 | 22 | 356 | 32 | 321 | 30 | NA | 700 | 0.2 | 24.2 | 1400000
2021-06-24 | 92540 | 92.54 | 7.55 | 7.61 | 157 | 23 | 324 | 30 | 294 | 28 | NA | 500 | 0.3 | 24 | 1600000
2021-06-25 | 91180 | 91.18 | 7.57 | 7.54 | 160 | 21 | 335 | 38 | 305 | 32 | NA | 600 | 0.2 | 24.1 | 1500000
2021-06-26 | 90550 | 90.55 | 7.52 | 7.58 | 126 | 20 | 347 | 34 | 311 | 30 | NA | 700 | 0.3 | 24.3 | 1400000
2021-06-27 | 82890 | 82.89 | 7.6 | 7.56 | 132 | 24 | 340 | 36 | 308 | 33 | NA | 600 | 0.2 | 24.2 | 1500000
2021-06-28 | 86130 | 86.13 | 7.45 | 7.59 | 138 | 20 | 354 | 37 | 315 | 32 | NA | 500 | 0.2 | 24.4 | 1600000
2021-06-29 | 82350 | 82.35 | 7.41 | 7.54 | 126 | 22 | 348 | 39 | 313 | 30 | NA | 600 | 0.3 | 24.3 | 1400000
2021-06-30 | 80460 | 80.46 | 7.47 | 7.58 | 135 | 18 | 338 | 42 | 319 | 33 | NA | 700 | 0.2 | 24.2 | 1300000
Average | 83947.1 | 83.9471 | 7.475 | 7.5647 | 149.4333 | 19.9333 | 350.6 | 37.4667 | 316 | 32.3 | NA | 620 | 0.24 | 24.1767 | 1423333.3333
2518.413
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 102360 | 102.36 | 7.63 | 7.66 | 163 | 26 |  |  | 332 | 35 |  | 800 | 0.4 | 24.5 | 1600000
Min | 59210 | 59.21 | 7.33 | 7.41 | 126 | 16 |  |  | 282 | 28 |  | 500 | 0.1 | 22.4 | 1200000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet BOD (Design- <500 mg/l) | Final BOD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-06-01 | 80200 | 80.2 | 7.42 | 7.7 | 125 | 19 | 288 | 44 | 252 | 28 | NA | 700 | 0.2 | 25.26 | 1400000 | 1) Rehabilitation works for STP, Mumfordganj SPS are in progress. 2) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 3) Retaining for nalla at tapping point for Rajapur SPS is broken hence raw sewage is going directly into the river.
2021-06-02 | 82560 | 82.56 | 7.45 | 7.64 | 130 | 18 | 292 | 48 | 247 | 29 | NA | 500 | 0.2 | 24.46 | 1700000
2021-06-03 | 80640 | 80.64 | 7.42 | 7.68 | 125 | 17 | 304 | 40 | 255 | 27 | NA | 400 | 0.3 | 22.05 | 1100000
2021-06-04 | 76820 | 76.82 | 7.4 | 7.69 | 135 | 14 | 320 | 44 | 262 | 26 | NA | 600 | 0.2 | 23.45 | 1300000
2021-06-05 | 76020 | 76.02 | 7.45 | 7.67 | 140 | 15 | 324 | 40 | 295 | 24 | NA | 500 | 0.2 | 26.32 | 1100000
2021-06-06 | 78770 | 78.77 | 7.42 | 7.65 | 130 | 15 | 316 | 40 | 286 | 28 | NA | 600 | 0.4 | 24.54 | 1700000
2021-06-07 | 81150 | 81.15 | 7.44 | 7.62 | 125 | 17 | 324 | 44 | 275 | 27 | NA | 500 | 0.2 | 25.45 | 1100000
2021-06-08 | 82100 | 82.1 | 7.45 | 7.68 | 130 | 18 | 328 | 44 | 297 | 25 | NA | 700 | 0.2 | 23.48 | 1700000
2021-06-09 | 80780 | 80.78 | 7.4 | 7.71 | 120 | 16 | 320 | 48 | 309 | 28 | NA | 400 | 0.3 | 22.58 | 1400000
2021-06-10 | 88060 | 88.06 | 7.42 | 7.72 | 135 | 19 | 328 | 40 | 312 | 26 | NA | 600 | 0.2 | 26.36 | 1300000
2021-06-11 | 87160 | 87.16 | 7.46 | 7.7 | 125 | 17 | 316 | 40 | 275 | 29 | NA | 400 | 0.2 | 27.5 | 1100000
2021-06-12 | 86410 | 86.41 | 7.43 | 7.68 | 130 | 15 | 288 | 48 | 254 | 28 | NA | 500 | 0.3 | 26.82 | 1700000
2021-06-13 | 83560 | 83.56 | 7.42 | 7.66 | 120 | 16 | 292 | 48 | 271 | 28 | NA | 400 | 0.2 | 27.42 | 1300000
2021-06-14 | 96750 | 96.75 | 7.48 | 7.67 | 125 | 19 | 288 | 44 | 287 | 26 | NA | 700 | 0.2 | 21.4 | 1400000
2021-06-15 | 100180 | 100.18 | 7.34 | 7.69 | 115 | 18 | 280 | 48 | 252 | 29 | NA | 400 | 0.3 | 23.58 | 1700000
2021-06-16 | 89410 | 89.41 | 7.35 | 7.65 | 125 | 17 | 316 | 48 | 273 | 25 | NA | 600 | 0.2 | 21.72 | 1700000
2021-06-17 | 84470 | 84.47 | 7.45 | 7.68 | 120 | 17 | 308 | 40 | 278 | 24 | NA | 500 | 0.2 | 22.5 | 1400000
2021-06-18 | 93090 | 93.09 | 7.56 | 7.65 | 115 | 19 | 280 | 44 | 248 | 29 | NA | 700 | 0.4 | 21.52 | 1100000
2021-06-19 | 98720 | 98.72 | 7.52 | 7.7 | 110 | 19 | 272 | 48 | 252 | 29 | NA | 400 | 0.2 | 23.46 | 1400000
2021-06-20 | 89810 | 89.81 | 7.43 | 7.72 | 120 | 16 | 292 | 40 | 272 | 27 | NA | 600 | 0.2 | 22.4 | 1100000
2021-06-21 | 83890 | 83.89 | 7.45 | 7.69 | 125 | 18 | 304 | 40 | 278 | 25 | NA | 400 | 0.3 | 23.56 | 1700000
2021-06-22 | 79740 | 79.74 | 7.42 | 7.7 | 135 | 14 | 320 | 36 | 262 | 24 | NA | 500 | 0.2 | 21.59 | 1400000
2021-06-23 | 85960 | 85.96 | 7.45 | 7.68 | 140 | 17 | 328 | 48 | 284 | 27 | NA | 400 | 0.2 | 22.74 | 1700000
2021-06-24 | 88960 | 88.96 | 7.42 | 7.69 | 125 | 18 | 312 | 44 | 266 | 28 | NA | 700 | 0.2 | 21.54 | 1300000
2021-06-25 | 83750 | 83.75 | 7.45 | 7.68 | 130 | 16 | 320 | 44 | 270 | 26 | NA | 400 | 0.3 | 22.05 | 1400000
2021-06-26 | 84590 | 84.59 | 7.42 | 7.71 | 120 | 19 | 308 | 40 | 284 | 25 | NA | 600 | 0.2 | 24.08 | 1100000
2021-06-27 | 85270 | 85.27 | 7.4 | 7.68 | 125 | 17 | 336 | 36 | 292 | 27 | NA | 700 | 0.4 | 25.32 | 1400000
2021-06-28 | 93500 | 93.5 | 7.43 | 7.65 | 115 | 19 | 328 | 40 | 282 | 29 | NA | 500 | 0.3 | 21.42 | 1100000
2021-06-29 | 82320 | 82.32 | 7.4 | 7.68 | 130 | 16 | 308 | 36 | 292 | 26 | NA | 500 | 0.2 | 22.8 | 1700000
2021-06-30 | 82250 | 82.25 | 7.41 | 7.69 | 125 | 17 | 296 | 40 | 273 | 25 | NA | 400 | 0.2 | 23.54 | 1300000
Average | 85563 | 85.563 | 7.432 | 7.6803 | 125.6667 | 17.0667 | 307.8667 | 42.8 | 274.5 | 26.8 | NA | 526.6667 | 0.24333 | 23.697 | 1393333.3333
2566.89
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 100180 | 100.18 | 7.56 | 7.72 | 140 | 19 |  |  | 312 | 29 |  | 700 | 0.4 | 27.5 | 1700000
Min | 76020 | 76.02 | 7.34 | 7.62 | 110 | 14 |  |  | 247 | 24 |  | 400 | 0.2 | 21.4 | 1100000