## Naini I
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-11-01 | 80460 | 80.46 | 7.33 | 7.48 | 136 | 20 | 328 | 40 | 283 | 31 | NA | 700 | 0.3 | 22.9 | 1300000 | Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2021-11-02 | 107700 | 107.7 | 7.39 | 7.51 | 129 | 19 | 320 | 36 | 286 | 33 | NA | 600 | 0.2 | 22.6 | 1200000
2021-11-03 | 112400 | 112.4 | 7.32 | 7.49 | 133 | 23 | 312 | 40 | 296 | 30 | NA | 400 | 0.3 | 22.2 | 1100000
2021-11-04 | 114140 | 114.14 | 7.41 | 7.52 | 126 | 20 | 324 | 44 | 302 | 32 | NA | 500 | 0.2 | 22.4 | 1700000
2021-11-05 | 112130 | 112.13 | 7.38 | 7.48 | 129 | 22 | 316 | 48 | 299 | 35 | NA | 700 | 0.3 | 22.6 | 1300000
2021-11-06 | 107330 | 107.33 | 7.44 | 7.53 | 136 | 20 | 320 | 40 | 292 | 33 | NA | 600 | 0.2 | 22.9 | 1400000
2021-11-07 | 106620 | 106.62 | 7.36 | 7.49 | 129 | 19 | 324 | 36 | 297 | 31 | NA | 500 | 0.3 | 22.8 | 1200000
2021-11-08 | 105550 | 105.55 | 7.43 | 7.58 | 133 | 21 | 328 | 44 | 303 | 33 | NA | 700 | 0.2 | 22.6 | 1300000
2021-11-09 | 108690 | 108.69 | 7.36 | 7.6 | 126 | 19 | 336 | 40 | 291 | 30 | NA | 500 | 0.3 | 22.8 | 1200000
2021-11-10 | 108520 | 108.52 | 7.29 | 7.44 | 133 | 18 | 340 | 36 | 298 | 32 | NA | 600 | 0.2 | 22.6 | 1400000
2021-11-11 | 113630 | 113.63 | 7.42 | 7.51 | 136 | 20 | 320 | 32 | 306 | 30 | NA | 400 | 0.3 | 23.4 | 1700000
2021-11-12 | 114760 | 114.76 | 7.38 | 7.63 | 126 | 20 | 336 | 36 | 312 | 28 | NA | 700 | 0.2 | 23.8 | 1300000
2021-11-13 | 113450 | 113.45 | 7.41 | 7.58 | 129 | 22 | 328 | 40 | 297 | 26 | NA | 500 | 0.3 | 22.9 | 1100000
2021-11-14 | 116700 | 116.7 | 7.36 | 7.49 | 133 | 20 | 320 | 44 | 303 | 29 | NA | 600 | 0.2 | 23.2 | 1700000
2021-11-15 | 117010 | 117.01 | 7.28 | 7.51 | 136 | 19 | 332 | 36 | 305 | 27 | NA | 400 | 0.3 | 23.4 | 1200000
2021-11-16 | 116430 | 116.43 | 7.33 | 7.46 | 126 | 21 | 312 | 40 | 299 | 29 | NA | 700 | 0.2 | 23.9 | 1400000
2021-11-17 | 113660 | 113.66 | 7.29 | 7.41 | 129 | 18 | 324 | 36 | 340 | 32 | NA | 500 | 0.3 | 23.7 | 1300000
2021-11-18 | 117200 | 117.2 | 7.35 | 7.52 | 139 | 17 | 336 | 32 | 325 | 30 | NA | 600 | 0.3 | 23.8 | 1700000
2021-11-19 | 116430 | 116.43 | 7.28 | 7.46 | 143 | 19 | 340 | 36 | 296 | 26 | NA | 400 | 0.2 | 23.4 | 1200000
2021-11-20 | 113220 | 113.22 | 7.33 | 7.49 | 129 | 20 | 320 | 40 | 302 | 28 | NA | 700 | 0.3 | 23.5 | 1400000
2021-11-21 | 112420 | 112.42 | 7.29 | 7.36 | 133 | 22 | 332 | 44 | 294 | 31 | NA | 500 | 0.2 | 23.7 | 1300000
2021-11-22 | 112190 | 112.19 | 7.36 | 7.44 | 126 | 18 | 316 | 36 | 303 | 29 | NA | 400 | 0.3 | 23.6 | 1200000
2021-11-23 | 114880 | 114.88 | 7.14 | 7.29 | 129 | 20 | 328 | 44 | 300 | 27 | NA | 600 | 0.2 | 23.5 | 1700000
2021-11-24 | 113000 | 113 | 7.21 | 7.44 | 136 | 17 | 336 | 36 | 298 | 30 | NA | 700 | 0.3 | 22.8 | 1300000
2021-11-25 | 114440 | 114.44 | 7.29 | 7.48 | 126 | 24 | 320 | 48 | 304 | 32 | NA | 500 | 0.2 | 23.4 | 1400000
2021-11-26 | 116920 | 116.92 | 7.33 | 7.43 | 139 | 21 | 344 | 40 | 307 | 29 | NA | 400 | 0.3 | 23.5 | 1200000
2021-11-27 | 117640 | 117.64 | 7.32 | 7.39 | 133 | 20 | 324 | 44 | 298 | 31 | NA | 600 | 0.2 | 22.9 | 1700000
2021-11-28 | 119380 | 119.38 | 7.44 | 7.59 | 136 | 18 | 332 | 36 | 304 | 33 | NA | 700 | 0.3 | 23.7 | 1300000
2021-11-29 | 116370 | 116.37 | 7.32 | 7.46 | 126 | 24 | 320 | 48 | 306 | 31 | NA | 500 | 0.2 | 22.2 | 1400000
2021-11-30 | 116590 | 116.59 | 7.36 | 7.49 | 129 | 20 | 316 | 40 | 299 | 29 | NA | 400 | 0.3 | 22.8 | 1200000
Average | 112328.6667 | 112.3287 | 7.34 | 7.485 | 131.6333 | 20.0333 | 326.1333 | 39.7333 | 301.5 | 30.2333 | NA | 553.3333 | 0.25333 | 23.1167 | 1360000
3369.86
Source: | Logbook of Labarotory at Sewage Treament Plant

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-11-01 | 86440 | 86.44 | 7.38 | 7.68 | 155 | 18 | 348 | 48 | 276 | 28 | NA | 500 | 0.2 | 26.52 | 1100000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Retaining wall of tapping point for Rajapur SPS is broken.
2021-11-02 | 80050 | 80.05 | 7.34 | 7.65 | 140 | 16 | 332 | 40 | 292 | 26 | NA | 400 | 0.3 | 23.88 | 1100000
2021-11-03 | 80760 | 80.76 | 7.36 | 7.69 | 135 | 17 | 340 | 44 | 308 | 25 | NA | 700 | 0.2 | 21.58 | 1400000
2021-11-04 | 72820 | 72.82 | 7.34 | 7.65 | 152 | 18 | 348 | 40 | 312 | 24 | NA | 600 | 0.2 | 24.56 | 1700000
2021-11-05 | 71150 | 71.15 | 7.3 | 7.67 | 130 | 14 | 328 | 40 | 288 | 26 | NA | 500 | 0.2 | 25.88 | 1200000
2021-11-06 | 71500 | 71.5 | 7.36 | 7.65 | 145 | 16 | 320 | 44 | 296 | 27 | NA | 400 | 0.3 | 26.42 | 1100000
2021-11-07 | 74930 | 74.93 | 7.34 | 7.69 | 135 | 17 | 312 | 44 | 275 | 25 | NA | 700 | 0.2 | 27.38 | 1300000
2021-11-08 | 71020 | 71.02 | 7.35 | 7.71 | 140 | 15 | 328 | 40 | 298 | 24 | NA | 500 | 0.4 | 22.46 | 1700000
2021-11-09 | 72470 | 72.47 | 7.4 | 7.7 | 155 | 14 | 348 | 48 | 315 | 26 | NA | 600 | 0.2 | 21.34 | 1200000
2021-11-10 | 73080 | 73.08 | 7.42 | 7.68 | 130 | 15 | 316 | 40 | 276 | 25 | NA | 700 | 0.2 | 23.52 | 1700000
2021-11-11 | 73580 | 73.58 | 7.38 | 7.67 | 135 | 16 | 320 | 44 | 265 | 27 | NA | 600 | 0.3 | 22.48 | 1400000
2021-11-12 | 77360 | 77.36 | 7.39 | 7.68 | 140 | 17 | 328 | 40 | 284 | 28 | NA | 400 | 0.2 | 21.88 | 1400000
2021-11-13 | 73890 | 73.89 | 7.38 | 7.72 | 130 | 15 | 316 | 44 | 265 | 26 | NA | 700 | 0.2 | 22.08 | 1700000
2021-11-14 | 73800 | 73.8 | 7.36 | 7.71 | 135 | 19 | 320 | 36 | 292 | 23 | NA | 600 | 0.3 | 21.18 | 1200000
2021-11-15 | 76820 | 76.82 | 7.35 | 7.65 | 145 | 18 | 340 | 40 | 315 | 27 | NA | 500 | 0.2 | 22.52 | 1300000
2021-11-16 | 76730 | 76.73 | 7.38 | 7.69 | 140 | 16 | 344 | 48 | 304 | 29 | NA | 400 | 0.2 | 23.42 | 1700000
2021-11-17 | 77790 | 77.79 | 7.36 | 7.67 | 135 | 15 | 328 | 40 | 263 | 28 | NA | 700 | 0.2 | 21.32 | 1400000
2021-11-18 | 80730 | 80.73 | 7.39 | 7.65 | 145 | 18 | 332 | 44 | 280 | 28 | NA | 600 | 0.3 | 22.84 | 1700000
2021-11-19 | 73350 | 73.35 | 7.42 | 7.75 | 155 | 17 | 348 | 40 | 315 | 24 | NA | 600 | 0.2 | 22.38 | 1100000
2021-11-20 | 77370 | 77.37 | 7.45 | 7.72 | 135 | 15 | 324 | 44 | 296 | 26 | NA | 700 | 0.2 | 23.46 | 1300000
2021-11-21 | 82910 | 82.91 | 7.41 | 7.73 | 130 | 18 | 320 | 40 | 290 | 27 | NA | 400 | 0.3 | 24.54 | 1200000
2021-11-22 | 71950 | 71.95 | 7.4 | 7.68 | 140 | 17 | 328 | 36 | 285 | 25 | NA | 500 | 0.3 | 26.4 | 1400000
2021-11-23 | 75910 | 75.91 | 7.38 | 7.65 | 152 | 19 | 348 | 44 | 276 | 26 | NA | 700 | 0.2 | 22.68 | 1100000
2021-11-24 | 76580 | 76.58 | 7.41 | 7.68 | 135 | 15 | 324 | 40 | 274 | 24 | NA | 600 | 0.2 | 21.78 | 1700000
2021-11-25 | 76590 | 76.59 | 7.42 | 7.65 | 140 | 24 | 340 | 48 | 284 | 28 | NA | 800 | 0.2 | 23.46 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Retaining wall of tapping point for Rajapur SPS is broken. 3) Aeration tank & Quiscent zone are bypassed on 25.11.2021 at 02:30 PM for cleaning of Quiscent zone. Currently, treatment of sewage is in process upto UASB only i.e., 50%.
2021-11-26 | 74800 | 74.8 | 7.38 | 7.21 | 130 | 38 | 316 | 64 | 252 | 48 | NA | 1200 | 0.2 | 21.32 | 1400000
2021-11-27 | 75080 | 75.08 | 7.36 | 7.51 | 135 | 40 | 324 | 96 | 286 | 62 | NA | 1400 | 0.2 | 26.56 | 1700000
2021-11-28 | 75390 | 75.39 | 7.39 | 7.53 | 155 | 37 | 344 | 104 | 292 | 82 | NA | 1300 | 0.2 | 24.34 | 1100000
2021-11-29 | 76190 | 76.19 | 7.42 | 7.51 | 140 | 39 | 348 | 112 | 310 | 84 | NA | 1400 | 0.2 | 22.38 | 1300000
2021-11-30 | 77590 | 77.59 | 7.45 | 7.54 | 130 | 40 | 320 | 108 | 272 | 80 | NA | 1300 | 0.2 | 21.46 | 1700000
Average | 75954.3333 | 75.9543 | 7.3823 | 7.6457 | 139.9667 | 20.4333 | 331.0667 | 51.3333 | 287.8667 | 33.6 | NA | 700 | 0.23 | 23.4007 | 1386666.6667
2278.63
Source: | Logbook of Labarotory at Sewage Treament Plant