## Naini I
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-10-01 | 98090 | 98.09 | 7.36 | 7.52 | 136 | 25 | 320 | 36 | 294 | 31 | NA | 700 | 0.3 | 23.4 | 1300000 | Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2021-10-02 | 98590 | 98.59 | 7.28 | 7.46 | 139 | 28 | 324 | 44 | 306 | 30 | NA | 500 | 0.2 | 24.3 | 1400000
2021-10-03 | 96470 | 96.47 | 7.36 | 7.53 | 129 | 24 | 316 | 40 | 301 | 28 | NA | 600 | 0.3 | 24.1 | 1200000
2021-10-04 | 98690 | 98.69 | 7.28 | 7.49 | 136 | 22 | 332 | 36 | 318 | 25 | NA | 400 | 0.2 | 23.4 | 1700000
2021-10-05 | 99270 | 99.27 | 7.33 | 7.45 | 133 | 25 | 320 | 44 | 305 | 27 | NA | 700 | 0.3 | 23.5 | 1100000
2021-10-06 | 102120 | 102.12 | 7.24 | 7.36 | 129 | 23 | 312 | 48 | 296 | 29 | NA | 600 | 0.2 | 24.2 | 1400000
2021-10-07 | 105730 | 105.73 | 7.33 | 7.46 | 139 | 21 | 332 | 40 | 298 | 26 | NA | 500 | 0.3 | 23.4 | 1300000
2021-10-08 | 106290 | 106.29 | 7.51 | 7.66 | 142 | 22 | 328 | 36 | 303 | 29 | NA | 400 | 0.4 | 23.7 | 1200000
2021-10-09 | 99890 | 99.89 | 7.41 | 7.63 | 129 | 24 | 316 | 44 | 307 | 27 | NA | 600 | 0.3 | 23.8 | 1700000
2021-10-10 | 102770 | 102.77 | 7.28 | 7.48 | 136 | 26 | 320 | 48 | 294 | 29 | NA | 500 | 0.4 | 22.05 | 1400000
2021-10-11 | 101280 | 101.28 | 7.32 | 7.39 | 133 | 22 | 324 | 40 | 288 | 39 | NA | 700 | 0.5 | 22.9 | 1300000
2021-10-12 | 99720 | 99.72 | 7.28 | 7.43 | 136 | 24 | 332 | 44 | 296 | 37 | NA | 400 | 0.3 | 23 | 1200000
2021-10-13 | 100410 | 100.41 | 7.32 | 7.49 | 129 | 23 | 328 | 40 | 299 | 33 | NA | 600 | 0.2 | 24 | 1100000
2021-10-14 | 105110 | 105.11 | 7.44 | 7.56 | 133 | 20 | 316 | 36 | 301 | 30 | NA | 500 | 0.2 | 24.3 | 1400000
2021-10-15 | 105210 | 105.21 | 7.35 | 7.47 | 142 | 25 | 324 | 48 | 295 | 35 | NA | 700 | 0.3 | 22.8 | 1300000
2021-10-16 | 101850 | 101.85 | 7.42 | 7.51 | 136 | 23 | 332 | 40 | 298 | 32 | NA | 400 | 0.2 | 23.8 | 1700000
2021-10-17 | 102430 | 102.43 | 7.45 | 7.62 | 133 | 21 | 336 | 36 | 312 | 30 | NA | 800 | 0.2 | 24.2 | 1200000
2021-10-18 | 97720 | 97.72 | 7.33 | 7.47 | 129 | 20 | 320 | 40 | 303 | 33 | NA | 600 | 0.3 | 24 | 1400000
2021-10-19 | 108560 | 108.56 | 7.27 | 7.39 | 133 | 22 | 332 | 36 | 309 | 31 | NA | 500 | 0.2 | 23.3 | 1300000
2021-10-20 | 107680 | 107.68 | 7.36 | 7.44 | 139 | 24 | 324 | 44 | 303 | 29 | NA | 700 | 0.3 | 22.9 | 1700000
2021-10-21 | 105170 | 105.17 | 7.44 | 7.56 | 129 | 22 | 316 | 40 | 298 | 32 | NA | 400 | 0.2 | 22.6 | 1200000
2021-10-22 | 106620 | 106.62 | 7.33 | 7.36 | 136 | 25 | 328 | 44 | 286 | 30 | NA | 600 | 0.3 | 22.5 | 1100000
2021-10-23 | 106260 | 106.26 | 7.28 | 7.44 | 133 | 23 | 320 | 36 | 294 | 33 | NA | 500 | 0.2 | 22.7 | 1300000
2021-10-24 | 105840 | 105.84 | 7.32 | 7.45 | 136 | 26 | 312 | 44 | 291 | 35 | NA | 700 | 0.3 | 23.4 | 1400000
2021-10-25 | 101320 | 101.32 | 7.38 | 7.52 | 129 | 22 | 316 | 40 | 278 | 31 | NA | 500 | 0.2 | 23.5 | 1200000
2021-10-26 | 55920 | 55.92 | 7.33 | 7.48 | 126 | 20 | 304 | 36 | 284 | 28 | NA | 600 | 0.3 | 23.2 | 1300000 | 1) Plant was taken into shutdown at 2:00 PM for installation of flowmeter in bypass line of Naini-I STP and replacement of NRV in header line of HNC pumps in Gaughat MPS. 2) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2021-10-27 | - | - | - | - | - | - | - | - | - | - | NA | - | - | - | - | Plant was taken into shutdown for installation of flowmeter in bypass line of Naini-I STP and replacement of NRV in header line of HNC pumps in Gaughat MPS.
2021-10-28 | - | - | - | - | - | - | - | - | - | - | NA | - | - | - | -
2021-10-29 | - | - | - | - | - | - | - | - | - | - | NA | - | - | - | -
2021-10-30 | 44610 | 44.61 | 7.36 | 7.48 | 133 | 22 | 320 | 44 | 293 | 35 | NA | 700 | 0.2 | 23.5 | 1200000 | 1) Plant was started at 4:00 PM after installation of flowmeter in bypass line of Naini-I STP. Replacement of NRV in header line of HNC pumps in Gaughat MPS was not completed. 2) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2021-10-31 | 91520 | 91.52 | 7.35 | 7.44 | 129 | 20 | 316 | 36 | 302 | 33 | NA | 500 | 0.3 | 23.8 | 1700000 | Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
Average | 98397.8571 | 98.3979 | 7.3468 | 7.4836 | 133.6429 | 23 | 322.1429 | 40.7143 | 298.2857 | 30.9643 | NA | 567.8571 | 0.27143 | 23.4375 | 1346428.5714
2755.14
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 44610 | 44.61 | 7.24 | 7.36 | 126 | 20 | 304 | 36 | 278 | 25 |  | 400 | 0.2 | 22.05 | 1100000
Max | 108560 | 108.56 | 7.51 | 7.66 | 142 | 28 | 336 | 48 | 318 | 39 |  | 800 | 0.5 | 24.3 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-10-01 | 84450 | 84.45 | 7.42 | 7.75 | 128 | 16 | 320 | 44 | 278 | 26 | NA | 700 | 0.3 | 23.58 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Retaining wall of tapping point for Rajapur SPS is broken.
2021-10-02 | 84210 | 84.21 | 7.45 | 7.71 | 122 | 18 | 312 | 40 | 270 | 28 | NA | 500 | 0.2 | 21.94 | 1100000
2021-10-03 | 78440 | 78.44 | 7.43 | 7.7 | 130 | 15 | 324 | 40 | 285 | 25 | NA | 400 | 0.2 | 22.86 | 1300000
2021-10-04 | 75470 | 75.47 | 7.42 | 7.72 | 140 | 18 | 328 | 44 | 292 | 27 | NA | 600 | 0.4 | 23.31 | 1400000
2021-10-05 | 75870 | 75.87 | 7.46 | 7.68 | 144 | 19 | 320 | 36 | 268 | 24 | NA | 700 | 0.2 | 21.84 | 1400000
2021-10-06 | 73930 | 73.93 | 7.42 | 7.69 | 150 | 18 | 324 | 48 | 280 | 26 | NA | 500 | 0.2 | 23.18 | 1700000
2021-10-07 | 73870 | 73.87 | 7.43 | 7.65 | 154 | 17 | 328 | 40 | 298 | 25 | NA | 400 | 0.2 | 22.46 | 1300000
2021-10-08 | 74260 | 74.26 | 7.48 | 7.68 | 138 | 15 | 320 | 44 | 275 | 27 | NA | 600 | 0.3 | 21.54 | 1400000
2021-10-09 | 76980 | 76.98 | 7.35 | 7.65 | 140 | 18 | 340 | 48 | 295 | 29 | NA | 700 | 0.2 | 23.84 | 1700000
2021-10-10 | 77320 | 77.32 | 7.32 | 7.68 | 130 | 15 | 344 | 40 | 290 | 26 | NA | 600 | 0.2 | 21.42 | 1300000
2021-10-11 | 72640 | 72.64 | 7.34 | 7.71 | 136 | 16 | 348 | 44 | 298 | 28 | NA | 400 | 0.3 | - | - | 1) Volute press pipe line connection work is in progress. Sludge was not drained. 2) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 3) Retaining wall of tapping point for Rajapur SPS is broken.
2021-10-12 | 76250 | 76.25 | 7.36 | 7.71 | 145 | 18 | 340 | 48 | 308 | 28 | NA | 700 | 0.2 | - | -
2021-10-13 | 76910 | 76.91 | 7.35 | 7.74 | 152 | 19 | 328 | 40 | 288 | 26 | NA | 400 | 0.2 | 22.52 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Retaining wall of tapping point for Rajapur SPS is broken.
2021-10-14 | 79360 | 79.36 | 7.31 | 7.69 | 140 | 16 | 320 | 40 | 265 | 25 | NA | 700 | 0.4 | 21.32 | 1400000
2021-10-15 | 80070 | 80.07 | 7.38 | 7.71 | 135 | 15 | 328 | 44 | 286 | 27 | NA | 400 | 0.2 | 23.5 | 1300000
2021-10-16 | 80720 | 80.72 | 7.39 | 7.73 | 130 | 17 | 340 | 48 | 308 | 28 | NA | 500 | 0.2 | 23.74 | 1700000
2021-10-17 | 80050 | 80.05 | 7.35 | 7.74 | 140 | 18 | 332 | 44 | 295 | 25 | NA | 700 | 0.2 | 24.56 | 1100000
2021-10-18 | 82050 | 82.05 | 7.32 | 7.71 | 145 | 18 | 320 | 40 | 275 | 26 | NA | 400 | 0.3 | 22.38 | 1400000
2021-10-19 | 86610 | 86.61 | 7.41 | 7.73 | 155 | 19 | 348 | 48 | 290 | 29 | NA | 500 | 0.2 | 21.54 | 1700000
2021-10-20 | 84850 | 84.85 | 7.42 | 7.7 | 125 | 17 | 328 | 44 | 268 | 28 | NA | 700 | 0.2 | 22.52 | 1400000
2021-10-21 | 80340 | 80.34 | 7.4 | 7.68 | 140 | 16 | 336 | 48 | 298 | 25 | NA | 500 | 0.2 | 23.58 | 1700000
2021-10-22 | 79240 | 79.24 | 7.36 | 7.7 | 152 | 18 | 348 | 48 | 318 | 27 | NA | 600 | 0.2 | 22.48 | 1100000
2021-10-23 | 78860 | 78.86 | 7.38 | 7.68 | 135 | 16 | 340 | 44 | 315 | 26 | NA | 500 | 0.3 | 21.56 | 1300000
2021-10-24 | 81330 | 81.33 | 7.36 | 7.65 | 130 | 17 | 320 | 48 | 288 | 28 | NA | 400 | 0.4 | 24.31 | 1300000
2021-10-25 | 86380 | 86.38 | 7.32 | 7.63 | 140 | 18 | 328 | 48 | 275 | 28 | NA | 400 | 0.2 | 23.58 | 1700000
2021-10-26 | 78800 | 78.8 | 7.35 | 7.68 | 135 | 18 | 316 | 40 | 280 | 25 | NA | 700 | 0.2 | 21.53 | 1400000
2021-10-27 | 83410 | 83.41 | 7.38 | 7.63 | 145 | 19 | 324 | 44 | 265 | 27 | NA | 600 | 0.2 | 23.8 | 1300000
2021-10-28 | 85910 | 85.91 | 7.35 | 7.71 | 152 | 17 | 328 | 48 | 286 | 28 | NA | 500 | 0.3 | 22.42 | 1400000
2021-10-29 | 82710 | 82.71 | 7.38 | 7.73 | 140 | 16 | 316 | 40 | 265 | 27 | NA | 400 | 0.2 | 21.36 | 1100000
2021-10-30 | 90140 | 90.14 | 7.35 | 7.7 | 135 | 18 | 320 | 48 | 286 | 29 | NA | 700 | 0.4 | 24.58 | 1700000
2021-10-31 | 84400 | 84.4 | 7.38 | 7.69 | 130 | 15 | 332 | 44 | 295 | 26 | NA | 500 | 0.2 | 23.56 | 1300000
Average | 80188.0645 | 80.1881 | 7.3813 | 7.6955 | 139.129 | 17.0968 | 329.0323 | 44 | 286.5484 | 26.7419 | NA | 545.1613 | 0.24516 | 22.7866 | 1424137.931
2485.83
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 72640 | 72.64 | 7.31 | 7.63 | 122 | 15 | 312 | 36 | 265 | 24 |  | 400 | 0.2 | 21.32 | 1100000
Max | 86610 | 90.14 | 7.48 | 7.75 | 155 | 19 | 348 | 48 | 318 | 29 |  | 700 | 0.4 | 24.58 | 1700000