## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-04-01 | 102930 | 102.93 | 7.28 | 7.34 | 146 | 22 | 364 | 44 | 306 | 30 | NA | 500 | 0.3 | 25.5 | 1700000 | 1) Only new line is in operation since maintenance work in new line from Gaughat MPS to Naini-I STP was in progress. 2) On 05.04.2022, sludge consistency was determined from slduge of sludge drying beds hence it cannot be deemed as accurate
2022-04-02 | 103160 | 103.16 | 7.31 | 7.39 | 139 | 20 | 348 | 40 | 304 | 32 | NA | 600 | 0.2 | 25.2 | 1400000
2022-04-03 | 103280 | 103.28 | 7.33 | 7.37 | 146 | 23 | 352 | 44 | 307 | 35 | NA | 400 | 0.3 | 25.3 | 1200000
2022-04-04 | 104200 | 104.2 | 7.32 | 7.36 | 136 | 18 | 344 | 36 | 309 | 33 | NA | 600 | 0.2 | 25.5 | 1400000
2022-04-05 | 97050 | 97.05 | 7.29 | 7.28 | 136 | 18 | 356 | 40 | 308 | 31 | NA | 400 | 0.3 | 25.9 | 1700000
2022-04-06 | 97140 | 97.14 | 7.31 | 7.39 | 143 | 22 | 344 | 44 | 312 | 29 | NA | 500 | 0.2 | 25.9 | 1100000
2022-04-07 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 25.6 | 1300000 | Gaughat MPS & Chacharnalla SPS were stopped and sewage was bypassed at 00:00 AM on 07.04.2022 due to installation of flowmeter in new line fom Gaughat MPS to Naini-I STP. Subsequently, Naini-I STP was also stopped.
2022-04-08 | 102150 | 102.15 | 7.28 | 7.35 | 129 | 24 | 340 | 48 | 306 | 32 | NA | 700 | 0.3 | 25 | 1300000 | Gaughat MPS & Chacharnalla SPS were started at 04:00 AM on 08.04.2022 after installation of flowmeter in new line fom Gaughat MPS to Naini-I STP. Subsequently, Naini-I STP was also started.
2022-04-09 | 118170 | 118.17 | 7.33 | 7.39 | 133 | 20 | 336 | 40 | 302 | 34 | NA | 500 | 0.2 | 25.2 | 1400000
2022-04-10 | 118170 | 118.17 | 7.33 | 7.37 | 129 | 18 | 344 | 36 | 306 | 32 | NA | 400 | 0.3 | 25.9 | 1700000
2022-04-11 | 117930 | 117.93 | 7.31 | 7.38 | 133 | 21 | 348 | 40 | 308 | 35 | NA | 600 | 0.2 | 25.8 | 1200000
2022-04-12 | 111050 | 111.05 | 7.33 | 7.39 | 136 | 23 | 352 | 44 | 302 | 33 | NA | 400 | 0.3 | 25.6 | 1300000
2022-04-13 | 108370 | 108.37 | 7.28 | 7.36 | 129 | 21 | 340 | 48 | 305 | 30 | NA | 500 | 0.2 | 25.8 | 1400000
2022-04-14 | 113540 | 113.54 | 7.33 | 7.38 | 136 | 20 | 340 | 44 | 307 | 32 | NA | 700 | 0.3 | 24.8 | 1400000 | On 14.04.2022 & 15.04.2022, sludge consistency was determined from sludge of sludge drying beds hence it cannot be deemed as accurate
2022-04-15 | 117330 | 117.33 | 7.31 | 7.35 | 129 | 18 | 336 | 36 | 303 | 31 | NA | 500 | 0.2 | 25.3 | 1200000
2022-04-16 | 118810 | 118.81 | 7.33 | 7.38 | 133 | 20 | 328 | 40 | 298 | 33 | NA | 600 | 0.3 | 25.6 | 1700000
2022-04-17 | 116830 | 116.83 | 7.28 | 7.35 | 136 | 21 | 340 | 48 | 301 | 35 | NA | 400 | 0.2 | 25.3 | 1300000
2022-04-18 | 118220 | 118.22 | 7.33 | 7.44 | 129 | 20 | 332 | 40 | 306 | 32 | NA | 700 | 0.3 | 25.2 | 1100000
2022-04-19 | 116860 | 116.86 | 7.35 | 7.39 | 133 | 18 | 336 | 36 | 302 | 34 | NA | 600 | 0.2 | 24.6 | 1200000 | On 19.04.2022, sludge consistency was determined from slduge of sludge drying beds hence it cannot be deemed as accurate
2022-04-20 | 120390 | 120.39 | 7.29 | 7.35 | 129 | 20 | 340 | 44 | 308 | 35 | NA | 500 | 0.3 | 25.4 | 1100000
2022-04-21 | 117340 | 117.34 | 7.32 | 7.38 | 136 | 22 | 352 | 40 | 298 | 33 | NA | 600 | 0.2 | 25.2 | 1400000
2022-04-22 | 117580 | 117.58 | 7.28 | 7.35 | 139 | 24 | 348 | 44 | 304 | 32 | NA | 400 | 0.3 | 25.6 | 1300000
2022-04-23 | 116330 | 116.33 | 7.33 | 7.38 | 143 | 22 | 352 | 48 | 306 | 34 | NA | 700 | 0.2 | 25.4 | 1700000
2022-04-24 | 113800 | 113.8 | 7.28 | 7.35 | 129 | 20 | 348 | 40 | 303 | 32 | NA | 500 | 0.3 | 25.5 | 1200000
2022-04-25 | 114680 | 114.68 | 7.35 | 7.38 | 136 | 18 | 328 | 36 | 306 | 35 | NA | 600 | 0.2 | 24.8 | 1300000
2022-04-26 | 121220 | 121.22 | 7.39 | 7.41 | 129 | 21 | 340 | 44 | 298 | 33 | NA | 400 | 0.3 | 25.4 | 1400000
2022-04-27 | 111240 | 111.24 | 7.32 | 7.44 | 126 | 23 | 328 | 48 | 305 | 30 | NA | 400 | 0.2 | 25.3 | 1500000
2022-04-28 | 114720 | 114.72 | 7.33 | 7.39 | 133 | 19 | 348 | 40 | 298 | 34 | NA | 700 | 0.2 | 25.3 | 1700000
2022-04-29 | 131970 | 131.97 | 7.28 | 7.36 | 129 | 20 | 336 | 44 | 303 | 31 | NA | 500 | 0.3 | 25.5 | 1300000
2022-04-30 | 122770 | 122.77 | 7.33 | 7.41 | 126 | 21 | 344 | 36 | 306 | 33 | NA | 400 | 0.2 | 25.4 | 1400000
Average | 109574.3333 | 109.5743 | 7.3148 | 7.3745 | 134 | 20.5862 | 342.8966 | 41.7931 | 304.3793 | 32.5862 | NA | 527.5862 | 0.24828 | 25.3933 | 1376666.6667
| 3287230 | 3287.23
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 97050 | 97.05 | 7.28 | 7.28 | 126 | 18 | 328 | 36 | 298 | 29 |  | 400 | 0.2 | 24.6 | 1100000
Max | 131970 | 131.97 | 7.39 | 7.44 | 146 | 24 | 364 | 48 | 312 | 35 |  | 700 | 0.3 | 25.9 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-04-01 | 56340 | 56.34 | 7.41 | 7.72 | 125 | 17 | 340 | 40 | 295 | 26 | NA | 500 | 0.2 | 22.84 | 1400000 | 1) On 01.04.2022, Mumfordganj SPS was started at 9:45 AM for after completion of works. 2) Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-04-02 | 78830 | 78.83 | 7.37 | 7.69 | 130 | 15 | 348 | 44 | 303 | 24 | NA | 600 | 0.2 | 21.75 | 1700000 | Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-04-03 | 75560 | 75.56 | 7.39 | 7.75 | 135 | 18 | 336 | 40 | 289 | 28 | NA | 400 | 0.2 | 22.95 | 1400000
2022-04-04 | 71210 | 71.21 | 7.38 | 7.7 | 135 | 17 | 344 | 44 | 307 | 25 | NA | 500 | 0.2 | 22.06 | 1700000
2022-04-05 | 71830 | 71.83 | 7.36 | 7.69 | 140 | 16 | 332 | 48 | 297 | 23 | NA | 600 | 0.2 | 22.93 | 1700000
2022-04-06 | 71230 | 71.23 | 7.41 | 7.73 | 132 | 15 | 340 | 44 | 288 | 27 | NA | 400 | 0.3 | 21.27 | 1400000
2022-04-07 | 74730 | 74.73 | 7.4 | 7.71 | 130 | 16 | 324 | 40 | 305 | 29 | NA | 500 | 0.2 | 23.63 | 1300000
2022-04-08 | 80570 | 80.57 | 7.37 | 7.68 | 140 | 19 | 328 | 44 | 309 | 26 | NA | 600 | 0.2 | 22.3 | 1700000
2022-04-09 | 74920 | 74.92 | 7.42 | 7.74 | 135 | 19 | 344 | 48 | 278 | 24 | NA | 400 | 0.2 | 21.59 | 1400000
2022-04-10 | 73530 | 73.53 | 7.37 | 7.69 | 125 | 16 | 332 | 36 | 295 | 28 | NA | 400 | 0.2 | 23.18 | 1300000
2022-04-11 | 70880 | 70.88 | 7.32 | 7.76 | 130 | 17 | 340 | 40 | 286 | 25 | NA | 500 | 0.2 | 22.48 | 1700000
2022-04-12 | 73300 | 73.3 | 7.39 | 7.72 | 135 | 18 | 336 | 44 | 297 | 27 | NA | 600 | 0.2 | 21.75 | 1700000
2022-04-13 | 75050 | 75.05 | 7.41 | 7.67 | 140 | 17 | 328 | 40 | 279 | 26 | NA | 500 | 0.3 | 22.27 | 1400000
2022-04-14 | 74310 | 74.31 | 7.35 | 7.69 | 135 | 19 | 348 | 44 | 301 | 24 | NA | 400 | 0.2 | 21.51 | 1300000
2022-04-15 | 74900 | 74.9 | 7.38 | 7.75 | 125 | 18 | 340 | 40 | 291 | 25 | NA | 500 | 0.2 | 22.75 | 1700000
2022-04-16 | 75150 | 75.15 | 7.42 | 7.73 | 140 | 19 | 332 | 48 | 285 | 28 | NA | 600 | 0.2 | 21.97 | 1400000
2022-04-17 | 80490 | 80.49 | 7.37 | 7.68 | 135 | 17 | 324 | 44 | 308 | 23 | NA | 400 | 0.3 | 22.79 | 1700000
2022-04-18 | 74610 | 74.61 | 7.43 | 7.79 | 130 | 18 | 344 | 40 | 295 | 27 | NA | 500 | 0.2 | 21.57 | 1700000
2022-04-19 | 77920 | 77.92 | 7.39 | 7.71 | 130 | 19 | 336 | 44 | 292 | 29 | NA | 600 | 0.2 | 22.25 | 1400000
2022-04-20 | 73730 | 73.73 | 7.44 | 7.75 | 125 | 17 | 328 | 40 | 307 | 24 | NA | 400 | 0.2 | 22.17 | 1300000
2022-04-21 | 75470 | 75.47 | 7.41 | 7.72 | 140 | 19 | 340 | 48 | 315 | 28 | NA | 400 | 0.2 | 22.93 | 1400000
2022-04-22 | 77950 | 77.95 | 7.36 | 7.69 | 135 | 18 | 332 | 44 | 294 | 25 | NA | 500 | 0.2 | 21.39 | 1700000
2022-04-23 | 79090 | 79.09 | 7.43 | 7.73 | 135 | 17 | 344 | 44 | 288 | 27 | NA | 600 | 0.3 | 22.37 | 1400000
2022-04-24 | 79840 | 79.84 | 7.4 | 7.62 | 140 | 16 | 336 | 40 | 296 | 29 | NA | 400 | 0.2 | 22.89 | 1700000
2022-04-25 | 77020 | 77.02 | 7.37 | 7.67 | 130 | 17 | 324 | 44 | 289 | 26 | NA | 600 | 0.2 | 21.76 | 1700000
2022-04-26 | 77970 | 77.97 | 7.41 | 7.7 | 135 | 16 | 332 | 40 | 305 | 24 | NA | 500 | 0.2 | 22.32 | 1400000
2022-04-27 | 79090 | 79.09 | 7.35 | 7.68 | 135 | 16 | 312 | 44 | 312 | 28 | NA | 600 | 0.2 | 23.15 | 1700000
2022-04-28 | 77650 | 77.65 | 7.42 | 7.69 | 130 | 17 | 336 | 40 | 297 | 25 | NA | 400 | 0.2 | 22.37 | 1300000
2022-04-29 | 83170 | 83.17 | 7.38 | 7.71 | 135 | 19 | 344 | 44 | 317 | 29 | NA | 500 | 0.2 | 21.83 | 1400000
2022-04-30 | 54050 | 54.05 | 7.43 | 7.68 | 140 | 14 | 328 | 36 | 282 | 23 | NA | 400 | 0.3 | 21.39 | 1400000 | 1) On 30.04.2022, Mumfordganj SPS was shutdown at 10:40 AM for diverting the rising main from Mumfordganj SPS to Rajapur STP due to ongoing construction of Expressway. 2) Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
Average | 74679.6667 | 74.6797 | 7.3913 | 7.708 | 133.5667 | 17.2 | 335.0667 | 42.5333 | 296.7333 | 26.0667 | NA | 493.3333 | 0.21667 | 22.2803 | 1513333.3333
| 2240390 | 2240.39
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 54050 | 54.05 | 7.32 | 7.62 | 125 | 14 | 312 | 36 | 278 | 23 |  | 400 | 0.2 | 21.27 | 1300000
Max | 83170 | 83.17 | 7.44 | 7.79 | 140 | 19 | 348 | 48 | 317 | 29 |  | 600 | 0.3 | 23.63 | 1700000