## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-08-01 | 116610 | 116.61 | 7.28 | 7.36 | 126 | 22 | 320 | 44 | 309 | 34 | NA | 400 | 0.3 | 25.3 | 1400000
2022-08-02 | 124240 | 124.24 | 7.26 | 7.33 | 123 | 20 | 312 | 40 | 298 | 35 | NA | 700 | 0.2 | 25.05 | 1700000
2022-08-03 | 124930 | 124.93 | 7.31 | 7.36 | 119 | 18 | 316 | 36 | 302 | 35 | NA | 500 | 0.3 | 25.3 | 1300000
2022-08-04 | 115740 | 115.74 | 7.29 | 7.35 | 126 | 17 | 312 | 36 | 316 | 37 | NA | 600 | 0.2 | 25.4 | 1200000
2022-08-05 | 117760 | 117.76 | 7.28 | 7.33 | 126 | 20 | 336 | 44 | 304 | 34 | NA | 400 | 0.3 | 25.4 | 1400000
2022-08-06 | 122440 | 122.44 | 7.36 | 7.39 | 123 | 18 | 320 | 40 | 303 | 34 | NA | 500 | 0.3 | 25.3 | 1300000
2022-08-07 | 122310 | 122.31 | 7.29 | 7.36 | 119 | 22 | 316 | 44 | 306 | 32 | NA | 600 | 0.3 | 24.7 | 1300000
2022-08-08 | 129570 | 129.57 | 7.31 | 7.35 | 126 | 18 | 312 | 36 | 298 | 30 | NA | 700 | 0.2 | 25.4 | 1700000
2022-08-09 | 123310 | 123.31 | 7.32 | 7.36 | 123 | 21 | 308 | 40 | 305 | 32 | NA | 500 | 0.3 | 25.2 | 1400000
2022-08-10 | 120370 | 120.37 | 7.29 | 7.33 | 119 | 17 | 304 | 36 | 302 | 33 | NA | 400 | 0.3 | 25 | 1200000
2022-08-11 | 118280 | 118.28 | 7.33 | 7.38 | 123 | 20 | 312 | 40 | 294 | 30 | NA | 500 | 0.2 | 25.2 | 1300000
2022-08-12 | 124510 | 124.51 | 7.39 | 7.41 | 126 | 21 | 308 | 44 | 296 | 28 | NA | 600 | 0.3 | 25.3 | 1700000
2022-08-13 | 118720 | 118.72 | 7.32 | 7.36 | 123 | 20 | 304 | 36 | 292 | 31 | NA | 700 | 0.2 | 25.4 | 1400000
2022-08-14 | 117530 | 117.53 | 7.33 | 7.38 | 119 | 18 | 308 | 32 | 296 | 29 | NA | 800 | 0.3 | 25.3 | 1300000
2022-08-15 | 113960 | 113.96 | 7.29 | 7.37 | 126 | 21 | 304 | 36 | 299 | 30 | NA | 400 | 0.3 | 25 | 1200000
2022-08-16 | 111020 | 111.02 | 7.33 | 7.41 | 129 | 20 | 312 | 40 | 302 | 28 | NA | 800 | 0.2 | 24.8 | 1400000
2022-08-17 | 118170 | 118.17 | 7.31 | 7.38 | 126 | 19 | 324 | 44 | 305 | 32 | NA | 700 | 0.2 | 25.1 | 1300000
2022-08-18 | 118040 | 118.04 | 7.33 | 7.36 | 123 | 20 | 308 | 40 | 306 | 33 | NA | 500 | 0.3 | 25.2 | 1700000
2022-08-19 | 130130 | 130.13 | 7.32 | 7.38 | 129 | 22 | 340 | 44 | 305 | 28 | NA | 600 | 0.2 | 25.1 | 1200000
2022-08-20 | 131330 | 131.33 | 7.29 | 7.36 | 133 | 20 | 352 | 40 | 313 | 30 | NA | 400 | 0.2 | 25.3 | 1300000
2022-08-21 | 121320 | 121.32 | 7.33 | 7.38 | 123 | 19 | 316 | 44 | 298 | 33 | NA | 700 | 0.3 | 25.3 | 1200000
2022-08-22 | 118980 | 118.98 | 7.27 | 7.37 | 126 | 20 | 344 | 40 | 305 | 31 | NA | 400 | 0.2 | 25.8 | 1100000
2022-08-23 | 101190 | 101.19 | 7.28 | 7.39 | 123 | 21 | 316 | 44 | 294 | 33 | NA | 500 | 0.4 | 25.4 | 1400000
2022-08-24 | 109210 | 109.21 | 7.33 | 7.36 | 119 | 18 | 304 | 36 | 296 | 31 | NA | 400 | 0.3 | 25.5 | 1700000
2022-08-25 | 114330 | 114.33 | 7.28 | 7.36 | 123 | 19 | 312 | 40 | 292 | 30 | NA | 600 | 0.2 | 25.2 | 1300000 | 1. Outlet gate for the effluent of STP was closed and bypass gate of Naini-I STP was opened at 10:00 PM on 25.08.2022. 2. Gaughat MPS is in operation but raw sewage pumped from it is bypassed before Naini-I STP on 25.08.2022. 3. Chacharnalla SPS is in operation but raw sewage pumped from it is bypassed before Gaughat MPS on 25.08.2022. 4. Currently, no sewage is coming to Naini-I STP.
2022-08-26 | 3790 | 3.79 | - | - | - | - | - | - | - | - | - | - | - | 25.3 | 1400000
2022-08-27 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | 25.4 | 1200000
2022-08-28 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | -
2022-08-29 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | -
2022-08-30 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | -
2022-08-31 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | -
Average | 96380.3226 | 96.3803 | 7.3088 | 7.3668 | 124.04 | 19.64 | 316.8 | 39.84 | 301.44 | 31.72 | NA | 556 | 0.26 | 25.2463 | 1370370.3704
2987.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.26 | 7.33 | 119 | 17 | 304 | 32 | 292 | 28 |  | 400 | 0.2 | 24.7 | 1100000
Max | 131330 | 131.33 | 7.39 | 7.41 | 133 | 22 | 352 | 44 | 316 | 37 |  | 800 | 0.4 | 25.8 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-08-01 | 81380 | 81.38 | 7.42 | 7.7 | 135 | 16 | 320 | 36 | 293 | 26 | NA | 600 | 0.2 | 24.67 | 1400000
2022-08-02 | 79030 | 79.03 | 7.38 | 7.75 | 130 | 18 | 332 | 40 | 287 | 28 | NA | 500 | 0.3 | 25.68 | 1700000
2022-08-03 | 79460 | 79.46 | 7.35 | 7.68 | 125 | 17 | 328 | 44 | 308 | 25 | NA | 600 | 0.2 | 24.41 | 1300000
2022-08-04 | 84900 | 84.9 | 7.39 | 7.63 | 135 | 18 | 336 | 40 | 285 | 26 | NA | 400 | 0.3 | 24.18 | 1200000
2022-08-05 | 79650 | 79.65 | 7.34 | 7.65 | 130 | 16 | 324 | 36 | 293 | 24 | NA | 500 | 0.3 | 25.35 | 1700000
2022-08-06 | 80830 | 80.83 | 7.42 | 7.73 | 135 | 17 | 332 | 40 | 305 | 27 | NA | 700 | 0.2 | 25.51 | 1400000
2022-08-07 | 81150 | 81.15 | 7.43 | 7.71 | 140 | 19 | 328 | 44 | 298 | 25 | NA | 400 | 0.2 | 25.23 | 1300000
2022-08-08 | 80730 | 80.73 | 7.37 | 7.72 | 125 | 18 | 316 | 40 | 288 | 28 | NA | 500 | 0.2 | 23.79 | 1200000
2022-08-09 | 79230 | 79.23 | 7.38 | 7.67 | 135 | 17 | 324 | 44 | 297 | 26 | NA | 600 | 0.3 | 24.97 | 1700000
2022-08-10 | 80310 | 80.31 | 7.32 | 7.78 | 130 | 16 | 332 | 36 | 289 | 27 | NA | 400 | 0.2 | 22.98 | 1400000
2022-08-11 | 80550 | 80.55 | 7.41 | 7.75 | 135 | 19 | 336 | 44 | 293 | 29 | NA | 500 | 0.2 | 24.75 | 1700000
2022-08-12 | 78010 | 78.01 | 7.41 | 7.73 | 125 | 16 | 324 | 40 | 287 | 26 | NA | 600 | 0.2 | 23.17 | 1400000
2022-08-13 | 75920 | 75.92 | 7.47 | 7.71 | 130 | 17 | 316 | 36 | 285 | 25 | NA | 400 | 0.3 | 23.94 | 1300000
2022-08-14 | 86180 | 86.18 | 7.43 | 7.68 | 125 | 18 | 328 | 40 | 281 | 23 | NA | 500 | 0.3 | 25.27 | 1400000
2022-08-15 | 73930 | 73.93 | 7.38 | 7.67 | 130 | 16 | 320 | 36 | 295 | 27 | NA | 600 | 0.2 | 24.53 | 1200000
2022-08-16 | 78210 | 78.21 | 7.35 | 7.62 | 135 | 17 | 324 | 36 | 275 | 24 | NA | 400 | 0.2 | 24.32 | 1300000
2022-08-17 | 75900 | 75.9 | 7.42 | 7.7 | 125 | 18 | 316 | 40 | 297 | 25 | NA | 500 | 0.3 | 25.23 | 1200000
2022-08-18 | 62320 | 62.32 | 7.38 | 7.65 | 130 | 17 | 320 | 36 | 285 | 23 | NA | 400 | 0.2 | 25.64 | 1100000 | 1. Inlet gate at tapping point for nearby drain of Rajapur SPS was closed at around 1:00 PM on 18.08.2022 due to rise in water level of Ganga river due to flood. 2. Mumfordganj SPS was in operation but scour valve in rising main was opened at 9:30 AM on 19.08.2022 for bypassing sewage as Rajapur STP was not in operation due to flood. 3. Currently, raw sewage due to leakage in inlet valve and seepage of water through ground due to flood is coming in STP.
2022-08-19 | 18400 | 18.4 | 7.31 | 7.53 | 110 | 15 | 152 | 20 | 170 | 18 | NA | - | - | 24.15 | 1200000
2022-08-20 | 5160 | 5.16 | 7.29 | 7.52 | 85 | 10 | 140 | 16 | 135 | 15 | NA | - | - | - | -
2022-08-21 | 6140 | 6.14 | 7.27 | 7.55 | 90 | 11 | 144 | 20 | 139 | 17 | NA | - | - | 24.17 | 1400000
2022-08-22 | 6240 | 6.24 | 7.43 | 7.53 | 85 | 10 | 152 | 20 | 135 | 15 | NA | 800 | - | 25.23 | 1300000
2022-08-23 | 6070 | 6.07 | 7.34 | 7.79 | 80 | 10 | 140 | 20 | 139 | 23 | NA | 900 | - | 23.51 | 1200000
2022-08-24 | 6540 | 6.54 | 7.45 | 7.88 | 55 | 9 | 96 | 16 | 76 | 21 | NA | 800 | - | 23.65 | 1300000
2022-08-25 | 7330 | 7.33 | 7.47 | 7.92 | 60 | 11 | 92 | 20 | 79 | 17 | NA | 900 | - | 24.58 | 1200000
2022-08-26 | 6180 | 6.18 | 7.43 | 7.87 | 50 | 9 | 88 | 16 | 81 | 15 | NA | 700 | - | 25.2 | 1100000
2022-08-27 | 7850 | 7.85 | 7.42 | 7.89 | 55 | 10 | 96 | 20 | 83 | 16 | NA | - | - | - | -
2022-08-28 | 8930 | 8.93 | 7.45 | 7.83 | 60 | 11 | 92 | 24 | 75 | 14 | NA | - | - | - | -
2022-08-29 | 9670 | 9.67 | 7.41 | 7.79 | 65 | 9 | 96 | 20 | 78 | 16 | NA | - | - | - | -
2022-08-30 | 12780 | 12.78 | 7.29 | 7.82 | 55 | 10 | 92 | 16 | 81 | 15 | NA | - | - | - | -
2022-08-31 | 14760 | 14.76 | 7.35 | 7.78 | 60 | 11 | 112 | 24 | 87 | 16 | NA | - | - | - | -
Average | 49475.4839 | 49.4755 | 7.3858 | 7.7171 | 105.3226 | 14.3871 | 237.0323 | 30.9677 | 212.871 | 22 | NA | 573.913 | 0.23889 | 24.5644 | 1344000
1533.74
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 5160 | 5.16 | 7.27 | 7.52 | 50 | 9 | 88 | 16 | 75 | 14 |  | 400 | 0.2 | 22.98 | 1100000
Max | 86180 | 86.18 | 7.47 | 7.92 | 140 | 19 | 336 | 44 | 308 | 29 |  | 900 | 0.3 | 25.68 | 1700000