## Naini I
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-12-01 | 116600 | 116.6 | 7.33 | 7.46 | 133 | 22 | 328 | 40 | 306 | 34 | NA | 600 | 0.3 | 22.6 | 1300000 | Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2021-12-02 | 117940 | 117.94 | 7.41 | 7.53 | 133 | 20 | 336 | 44 | 308 | 32 | NA | 500 | 0.2 | 23.1 | 1200000
2021-12-03 | 119650 | 119.65 | 7.32 | 7.45 | 126 | 21 | 324 | 36 | 303 | 30 | NA | 700 | 0.3 | 22.8 | 1400000
2021-12-04 | 116010 | 116.01 | 7.51 | 7.61 | 129 | 20 | 316 | 40 | 293 | 33 | NA | 400 | 0.2 | 23.1 | 1300000
2021-12-05 | 116400 | 116.4 | 7.46 | 7.52 | 136 | 24 | 328 | 48 | 303 | 29 | NA | 600 | 0.3 | 23.7 | 1700000
2021-12-06 | 118380 | 118.38 | 7.36 | 7.46 | 133 | 18 | 320 | 36 | 305 | 31 | NA | 500 | 0.2 | 23.13 | 1200000
2021-12-07 | 115750 | 115.75 | 7.44 | 7.51 | 136 | 20 | 336 | 44 | 296 | 33 | NA | 700 | 0.3 | 22.85 | 1300000
2021-12-08 | 112720 | 112.72 | 7.33 | 7.44 | 129 | 19 | 324 | 40 | 302 | 30 | NA | 400 | 0.2 | 22.4 | 1400000
2021-12-09 | 114830 | 114.83 | 7.29 | 7.38 | 133 | 21 | 336 | 48 | 298 | 28 | NA | 600 | 0.3 | 22.9 | 1700000
2021-12-10 | 118100 | 118.1 | 7.33 | 7.51 | 139 | 18 | 340 | 40 | 302 | 31 | NA | 500 | 0.2 | 23.2 | 1200000
2021-12-11 | 116220 | 116.22 | 7.28 | 7.44 | 129 | 17 | 332 | 36 | 296 | 29 | NA | 700 | 0.3 | 22.9 | 1300000
2021-12-12 | 112120 | 112.12 | 7.33 | 7.41 | 126 | 20 | 324 | 44 | 305 | 35 | NA | 400 | 0.2 | 23.2 | 1400000
2021-12-13 | 113920 | 113.92 | 7.29 | 7.36 | 129 | 22 | 336 | 40 | 299 | 32 | NA | 600 | 0.3 | 23.3 | 1200000
2021-12-14 | 110750 | 110.75 | 7.32 | 7.41 | 126 | 18 | 320 | 36 | 303 | 28 | NA | 500 | 0.2 | 22.6 | 1300000
2021-12-15 | 111050 | 111.05 | 7.33 | 7.44 | 133 | 20 | 332 | 44 | 298 | 31 | NA | 600 | 0.3 | 23.4 | 1400000
2021-12-16 | 110820 | 110.82 | 7.35 | 7.42 | 126 | 19 | 324 | 40 | 300 | 33 | NA | 700 | 0.3 | 22.8 | 1200000
2021-12-17 | 114160 | 114.16 | 7.36 | 7.45 | 136 | 17 | 340 | 36 | 307 | 35 | NA | 400 | 0.2 | 23.6 | 1700000
2021-12-18 | 110230 | 110.23 | 7.33 | 7.38 | 129 | 21 | 332 | 44 | 305 | 32 | NA | 500 | 0.3 | 23.5 | 1300000
2021-12-19 | 115540 | 115.54 | 7.36 | 7.39 | 133 | 23 | 344 | 48 | 309 | 34 | NA | 600 | 0.2 | 23.2 | 1400000
2021-12-20 | 106750 | 106.75 | 7.29 | 7.41 | 139 | 21 | 352 | 40 | 305 | 32 | NA | 400 | 0.3 | 23.03 | 1300000
2021-12-21 | 113420 | 113.42 | 7.33 | 7.39 | 129 | 18 | 328 | 36 | 302 | 31 | NA | 700 | 0.2 | 21.14 | 1700000
2021-12-22 | 111790 | 111.79 | 7.51 | 7.56 | 133 | 20 | 336 | 44 | 306 | 35 | NA | 500 | 0.3 | 23.12 | 1200000
2021-12-23 | 133200 | 133.2 | 7.53 | 7.58 | 139 | 20 | 352 | 40 | 297 | 28 | NA | 700 | 0.2 | 23 | 1400000
2021-12-24 | 105970 | 105.97 | 7.44 | 7.52 | 136 | 22 | 348 | 44 | 302 | 31 | NA | 600 | 0.3 | 22.7 | 1300000
2021-12-25 | 110540 | 110.54 | 7.29 | 7.39 | 126 | 19 | 328 | 40 | 299 | 33 | NA | 400 | 0.2 | 22.9 | 1100000
2021-12-26 | 108440 | 108.44 | 7.33 | 7.41 | 133 | 21 | 344 | 44 | 305 | 35 | NA | 400 | 0.3 | 23.3 | 1200000
2021-12-27 | 110860 | 110.86 | 7.29 | 7.38 | 139 | 23 | 356 | 48 | 301 | 32 | NA | 700 | 0.2 | 23.25 | 1400000
2021-12-28 | 116630 | 116.63 | 7.36 | 7.41 | 133 | 20 | 348 | 40 | 309 | 34 | NA | 500 | 0.3 | 23.9 | 1700000
2021-12-29 | 113660 | 113.66 | 7.29 | 7.36 | 143 | 18 | 352 | 36 | 304 | 31 | NA | 600 | 0.3 | 24.1 | 1300000
2021-12-30 | 115020 | 115.02 | 7.33 | 7.38 | 129 | 21 | 332 | 44 | 308 | 33 | NA | 700 | 0.2 | 23.84 | 1400000
2021-12-31 | 115160 | 115.16 | 7.29 | 7.36 | 133 | 23 | 340 | 48 | 302 | 32 | NA | 400 | 0.3 | 23.6 | 1200000
Average | 114278.3871 | 114.2784 | 7.3552 | 7.4426 | 132.4516 | 20.1935 | 335.0968 | 41.5484 | 302.5161 | 31.8387 | NA | 551.6129 | 0.25484 | 23.1019 | 1358064.5161
3542.63
Min | 105970 | 105.97 | 7.28 | 7.36 | 126 | 17 | 316 | 36 | 293 | 28 |  | 400 | 0.2 | 21.14 | 1100000
Max | 133200 | 133.2 | 7.53 | 7.61 | 143 | 24 | 356 | 48 | 309 | 35 |  | 700 | 0.3 | 24.1 | 1700000
Source: | Logbook of Labarotory at Sewage Treament Plant

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-12-01 | 75880 | 75.88 | 7.35 | 7.58 | 125 | 37 | 316 | 104 | 258 | 78 | NA | 1200 | 0.2 | 24.56 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Retaining wall of tapping point for Rajapur SPS is broken. 3) Aeration tank & Quiscent zone are bypassed on 25.11.2021 at 02:30 PM for cleaning of Quiscent zone. Currently, treatment of sewage is in process upto UASB only i.e., 50% hence the KPIs are out of range.
2021-12-02 | 75530 | 75.53 | 7.36 | 7.51 | 130 | 36 | 324 | 116 | 265 | 86 | NA | 1400 | 0.2 | 23.54 | 1700000
2021-12-03 | 76400 | 76.4 | 7.38 | 7.56 | 140 | 39 | 332 | 108 | 280 | 81 | NA | 1200 | 0.2 | 21.56 | 1300000
2021-12-04 | 76120 | 76.12 | 7.35 | 7.55 | 135 | 35 | 340 | 104 | 285 | 85 | NA | 1300 | 0.2 | 24.34 | 1400000
2021-12-05 | 76030 | 76.03 | 7.36 | 7.58 | 155 | 37 | 348 | 112 | 302 | 80 | NA | 1300 | 0.2 | 21.82 | 1100000
2021-12-06 | 74610 | 74.61 | 7.39 | 7.56 | 130 | 38 | 316 | 104 | 292 | 78 | NA | 1200 | 0.2 | 23.54 | 1400000
2021-12-07 | 71680 | 71.68 | 7.32 | 7.54 | 140 | 35 | 312 | 108 | 268 | 82 | NA | 1400 | 0.3 | 21.56 | 1700000
2021-12-08 | 40920 | 40.92 | 7.34 | 7.55 | 135 | 38 | 328 | 112 | 285 | 79 | NA | 1100 | 0.2 | 24.32 | 1700000 | 1) Raw water received at STP is less due to maintenance in sewage line from Alopibagh SPS to Mumfordganj SPS. 2) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 3) Retaining wall of tapping point for Rajapur SPS is broken. 4) Aeration tank & Quiscent zone are bypassed on 25.11.2021 at 02:30 PM for cleaning of Quiscent zone. Currently, treatment of sewage is in process upto UASB only i.e., 50% hence the KPIs are out of range.
2021-12-09 | 65270 | 65.27 | 7.35 | 7.56 | 140 | 35 | 320 | 104 | 295 | 70 | NA | 1200 | 0.1 | 23.22 | 1300000
2021-12-10 | 64810 | 64.81 | 7.38 | 7.54 | 130 | 36 | 340 | 108 | 260 | 72 | NA | 1300 | 0.1 | 22.56 | 1400000
2021-12-11 | 55000 | 55 | 7.35 | 7.56 | 155 | 37 | 332 | 112 | 286 | 78 | NA | 1200 | 0.2 | 21.32 | 1400000
2021-12-12 | 32260 | 32.26 | 7.39 | 7.52 | 135 | 34 | 320 | 108 | 296 | 75 | NA | 1100 | 0.2 | 23.54 | 1700000
2021-12-13 | 72310 | 72.31 | 7.36 | 7.58 | 130 | 36 | 328 | 104 | 275 | 78 | NA | 1300 | 0.1 | 21.52 | 1300000 | 1) Upto 26.11.2021, sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Retaining wall of tapping point for Rajapur SPS is broken. 3) Aeration tank & Quiscent zone are bypassed on 25.11.2021 at 02:30 PM for cleaning of Quiscent zone. Currently, treatment of sewage is in process upto UASB only i.e., 50% hence the KPIs are out of range. 4) Sludge dewatering buidling is started on 27.12.2021.
2021-12-14 | 74280 | 74.28 | 7.38 | 7.54 | 145 | 37 | 336 | 100 | 292 | 72 | NA | 1300 | 0.1 | 23.24 | 1400000
2021-12-15 | 73230 | 73.23 | 7.36 | 7.56 | 135 | 35 | 348 | 108 | 286 | 70 | NA | 1400 | 0.1 | 22.53 | 1100000
2021-12-16 | 75630 | 75.63 | 7.38 | 7.53 | 140 | 38 | 320 | 112 | 268 | 74 | NA | 1200 | 0.2 | 24.48 | 1700000
2021-12-17 | 74700 | 74.7 | 7.37 | 7.6 | 155 | 36 | 328 | 108 | 280 | 76 | NA | 1400 | 0.1 | 21.8 | 1300000
2021-12-18 | 72830 | 72.83 | 7.35 | 7.56 | 135 | 38 | 316 | 112 | 292 | 72 | NA | 1100 | 0.1 | 22.34 | 1400000
2021-12-19 | 72590 | 72.59 | 7.36 | 7.58 | 140 | 39 | 332 | 116 | 269 | 75 | NA | 1300 | 0.1 | 21.52 | 1700000
2021-12-20 | 76950 | 76.95 | 7.35 | 7.52 | 130 | 37 | 320 | 108 | 258 | 70 | NA | 1300 | 0.2 | 22.58 | 1400000
2021-12-21 | 74630 | 74.63 | 7.38 | 7.5 | 140 | 38 | 328 | 112 | 274 | 76 | NA | 1400 | 0.1 | 24.66 | 1700000
2021-12-22 | 76910 | 76.91 | 7.35 | 7.56 | 155 | 34 | 348 | 112 | 288 | 78 | NA | 1100 | 0.1 | 23.18 | 1700000
2021-12-23 | 72710 | 72.71 | 7.38 | 7.51 | 135 | 39 | 340 | 116 | 279 | 82 | NA | 1200 | 0.1 | 25.23 | 1400000
2021-12-24 | 75920 | 75.92 | 7.34 | 7.52 | 130 | 37 | 328 | 112 | 256 | 77 | NA | 1400 | 0.2 | 21.08 | 1100000
2021-12-25 | 72340 | 72.34 | 7.36 | 7.58 | 135 | 36 | 320 | 108 | 292 | 75 | NA | 1300 | 0.1 | 22.32 | 1300000
2021-12-26 | 77860 | 77.86 | 7.35 | 7.56 | 125 | 38 | 324 | 116 | 266 | 79 | NA | 1200 | 0.1 | 21.48 | 1700000
2021-12-27 | 73080 | 73.08 | 7.37 | 7.58 | 140 | 35 | 340 | 108 | 298 | 76 | NA | 1300 | 0.1 | 27.48 | 1700000
2021-12-28 | 76110 | 76.11 | 7.45 | 7.6 | 155 | 34 | 348 | 112 | 308 | 74 | NA | 1400 | 0.2 | 22.78 | 1400000
2021-12-29 | 72550 | 72.55 | 7.46 | 7.61 | 130 | 36 | 332 | 120 | 302 | 86 | NA | 1100 | 0.1 | 23.56 | 1300000 | 1) Retaining wall of tapping point for Rajapur SPS is broken. 2) Aeration tank & Quiscent zone are started at 7:30 PM on 29.12.2021 after cleaning of Quiscent zone. Only 35-40% cleaning of Quiescent zone is completed but in view of Magh mela, cleaning work is stopped for now.
2021-12-30 | 72880 | 72.88 | 7.48 | 7.62 | 135 | 30 | 328 | 88 | 284 | 70 | NA | 1200 | - | 22.95 | 1400000 | 1) Retaining wall of tapping point for Rajapur SPS is broken. 2) CCT is byppased from 7:00 PM on 29.12.2021 to 12:00 PM on 31.12.2021, for bypassing extra TSS coming in effluent due to clenaing work and preventing it from depositing in CCT. 3) Values of KPIs are out of range as generation of culture is not upto the mark in biological units.
2021-12-31 | 74740 | 74.74 | 7.5 | 7,68 | 110 | 24 | 272 | 60 | 232 | 51 | NA | 1100 | 0.2 | 23.42 | 1700000
Average | 70863.2258 | 70.8632 | 7.3758 | 7.5573 | 137.0968 | 35.9355 | 327.871 | 107.4839 | 279.7097 | 75.9677 | NA | 1254.8387 | 0.15333 | 23.0332 | 1458064.5161
2196.76
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 32260 | 32.26 | 7.32 | 7.5 | 110 | 24 | 272 | 60 | 232 | 51 |  | 1100 | 0.1 | 21.08 | 1100000
Max | 77860 | 77.86 | 7.5 | 7.62 | 155 | 39 | 348 | 120 | 308 | 86 |  | 1400 | 0.3 | 27.48 | 1700000