## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-12-01 | 120390 | 120.39 | 7.29 | 7.33 | 140 | 23 | 338 | 43 | 307 | 29 | NA | 500 | 0.5 | 24.9 | 1700000
2022-12-02 | 117670 | 117.67 | 7.33 | 7.38 | 135 | 24 | 329 | 45 | 328 | 28 | NA | 600 | 0.4 | 23.8 | 1300000
2022-12-03 | 114920 | 114.92 | 7.16 | 7.22 | 140 | 25 | 335 | 40 | 302 | 29 | NA | 400 | 0.5 | 24.08 | 1400000
2022-12-04 | 110800 | 110.8 | 7.22 | 7.24 | 145 | 26 | 338 | 44 | 286 | 27 | NA | 700 | 0.4 | 24.8 | 1700000
2022-12-05 | 116410 | 116.41 | 7.29 | 7.31 | 130 | 23 | 324 | 43 | 294 | 30 | NA | 500 | 0.5 | 24.9 | 1200000
2022-12-06 | 115280 | 115.28 | 7.33 | 7.34 | 120 | 26 | 332 | 40 | 303 | 28 | NA | 700 | 0.3 | 24.5 | 1200000
2022-12-07 | 110300 | 110.3 | 7.13 | 6.98 | 135 | 23 | 330 | 42 | 292 | 30 | NA | 800 | 0.4 | 24.8 | 1700000
2022-12-08 | 108090 | 108.09 | 7.09 | 6.94 | 125 | 25 | 320 | 41 | 305 | 28 | NA | 600 | 0.5 | 24.03 | 1300000
2022-12-09 | 110590 | 110.59 | 7.18 | 7.22 | 145 | 24 | 336 | 43 | 294 | 26 | NA | 800 | 0.5 | 24.68 | 1700000
2022-12-10 | 105980 | 105.89 | 7.23 | 7.02 | 135 | 26 | 339 | 44 | 305 | 31 | NA | 500 | 0.4 | 24.66 | 1400000
2022-12-11 | 113900 | 113.9 | 7.18 | 7.2 | 130 | 23 | 324 | 42 | 299 | 30 | NA | 600 | 0.5 | 24.3 | 1200000
2022-12-12 | 115740 | 115.74 | 7.11 | 7.09 | 135 | 24 | 329 | 40 | 303 | 28 | NA | 700 | 0.3 | 24.32 | 1300000
2022-12-13 | 121350 | 121.35 | 7.16 | 7.11 | 125 | 25 | 336 | 42 | 292 | 29 | NA | 500 | 0.5 | 24.9 | 1700000
2022-12-14 | 120550 | 120.55 | 7.09 | 7.08 | 125 | 26 | 340 | 44 | 304 | 31 | NA | 700 | 0.4 | 24.36 | 1400000
2022-12-15 | 119610 | 119.61 | 7.13 | 7.11 | 130 | 24 | 329 | 43 | 299 | 32 | NA | 600 | 0.5 | 24.4 | 1300000
2022-12-16 | 119050 | 119.05 | 7.08 | 7.21 | 125 | 26 | 336 | 42 | 302 | 28 | NA | 500 | 0.3 | 24.5 | 1700000
2022-12-17 | 121340 | 121.34 | 7.12 | 7.35 | 135 | 24 | 328 | 44 | 312 | 33 | NA | 700 | 0.3 | 24.68 | 1200000
2022-12-18 | 117560 | 117.56 | 7.2 | 7.48 | 125 | 24 | 320 | 40 | 303 | 32 | NA | 600 | 0.4 | 24.36 | 1400000
2022-12-19 | 119190 | 119.19 | 7.16 | 7.51 | 140 | 25 | 326 | 42 | 305 | 31 | NA | 400 | 0.3 | 24.78 | 1300000
2022-12-20 | 125620 | 125.62 | 7.22 | 7.55 | 135 | 26 | 330 | 41 | 292 | 29 | NA | 800 | 0.4 | 24.8 | 1700000
2022-12-21 | 119190 | 119.19 | 7.2 | 7.46 | 130 | 24 | 336 | 43 | 305 | 30 | NA | 500 | 0.3 | 24.5 | 1300000
2022-12-22 | 106380 | 106.38 | 7.23 | 7.45 | 125 | 25 | 324 | 44 | 303 | 32 | NA | 700 | 0.4 | 24.9 | 1200000
2022-12-23 | 117510 | 117.51 | 7.17 | 7.42 | 138 | 26 | 329 | 46 | 292 | 28 | NA | 500 | 0.4 | 24.66 | 1400000
2022-12-24 | 116720 | 116.72 | 7.19 | 7.48 | 135 | 26 | 339 | 44 | 304 | 29 | NA | 400 | 0.4 | 24.9 | 1400000
2022-12-25 | 116890 | 116.89 | 7.13 | 7.45 | 138 | 24 | 320 | 43 | 294 | 28 | NA | 500 | 0.3 | 24.68 | 1300000
2022-12-26 | 118440 | 118.44 | 7.28 | 7.43 | 140 | 25 | 326 | 42 | 292 | 29 | NA | 400 | 0.4 | 24.8 | 1400000
2022-12-27 | 118450 | 118.45 | 7.33 | 7.4 | 125 | 24 | 308 | 46 | 304 | 32 | NA | 700 | 0.5 | 24.66 | 1200000
2022-12-28 | 111930 | 111.93 | 7.19 | 7.34 | 135 | 27 | 326 | 42 | 299 | 28 | NA | 600 | 0.4 | 25.4 | 1400000
2022-12-29 | 104280 | 104.28 | 7.21 | 7.45 | 130 | 26 | 336 | 44 | 305 | 26 | NA | 800 | 0.4 | 24.9 | 1300000
2022-12-30 | 119710 | 119.71 | 7.32 | 7.42 | 140 | 25 | 324 | 40 | 316 | 30 | NA | 700 | 0.3 | 24.32 | 1700000
2022-12-31 | 188910 | 118.91 | 7.31 | 7.38 | 125 | 28 | 336 | 43 | 314 | 32 | NA | 800 | 0.2 | 24.38 | 1400000
Average | 118153.2258 | 115.8923 | 7.2019 | 7.3016 | 132.7742 | 24.9032 | 329.7742 | 42.6452 | 301.7742 | 29.4516 | NA | 606.4516 | 0.39677 | 24.6016 | 1412903.2258
3592.66
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 104280 | 104.28 | 7.08 | 6.94 | 120 | 23 | 308 | 40 | 286 | 26 |  | 400 | 0.2 | 23.8 | 1200000
Max | 188910 | 125.62 | 7.33 | 7.55 | 145 | 28 | 340 | 46 | 328 | 33 |  | 800 | 0.5 | 25.4 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-12-01 | 78510 | 78.51 | 7.54 | 7.76 | 125 | 16 | 328 | 40 | 282 | 26 | NA | 600 | 0.2 | 24.6 | 1300000 | Retaining wall for the tapping point of Rajapur SPS is broken, hence raw sewage is going dirctly into the river.
2022-12-02 | 80120 | 80.12 | 7.49 | 7.72 | 135 | 17 | 344 | 44 | 268 | 25 | NA | 500 | 0.3 | 23.8 | 1400000
2022-12-03 | 80370 | 80.37 | 7.52 | 7.65 | 140 | 18 | 348 | 48 | 315 | 24 | NA | 700 | 0.2 | 24.15 | 1700000
2022-12-04 | 80270 | 80.2 | 7.46 | 7.66 | 145 | 19 | 336 | 44 | 291 | 26 | NA | 400 | 0.2 | 23.38 | 1400000
2022-12-05 | 78460 | 78.46 | 7.38 | 7.64 | 150 | 18 | 332 | 40 | 284 | 25 | NA | 500 | 0.3 | 23.47 | 1300000
2022-12-06 | 80800 | 80.8 | 7.35 | 7.61 | 130 | 17 | 328 | 44 | 273 | 26 | NA | 600 | 0.2 | 24.97 | 1700000
2022-12-07 | 79210 | 79.21 | 7.28 | 7.62 | 135 | 18 | 316 | 40 | 291 | 25 | NA | 500 | 0.2 | 24.26 | 1400000
2022-12-08 | 79090 | 79.09 | 7.14 | 7.57 | 130 | 17 | 308 | 44 | 298 | 26 | NA | 700 | 0.3 | 24.02 | 1300000
2022-12-09 | 78810 | 78.81 | 7.1 | 7.58 | 115 | 18 | 312 | 40 | 297 | 24 | NA | 600 | 0.2 | 23.21 | 1400000
2022-12-10 | 81050 | 81.05 | 7.36 | 7.6 | 130 | 19 | 336 | 48 | 305 | 27 | NA | 700 | 0.2 | 24.9 | 1400000
2022-12-11 | 81370 | 81.37 | 7.45 | 7.59 | 135 | 18 | 332 | 44 | 283 | 25 | NA | 600 | 0.3 | 24.22 | 1700000
2022-12-12 | 78010 | 78.01 | 7.6 | 7.6 | 130 | 16 | 324 | 40 | 291 | 24 | NA | 500 | 0.2 | 23.26 | 1300000
2022-12-13 | 80870 | 80.87 | 7.45 | 7.62 | 125 | 17 | 320 | 44 | 270 | 27 | NA | 700 | 0.2 | 24.39 | 1400000
2022-12-14 | 77490 | 77.49 | 7.26 | 7.59 | 135 | 19 | 328 | 48 | 283 | 28 | NA | 600 | 0.3 | 25.56 | 1300000
2022-12-15 | 80140 | 80.14 | 7.18 | 7.57 | 130 | 18 | 316 | 44 | 307 | 29 | NA | 700 | 0.2 | 24.21 | 1400000
2022-12-16 | 76820 | 76.82 | 7.32 | 7.59 | 135 | 17 | 336 | 40 | 289 | 26 | NA | 500 | 0.2 | 23.42 | 1700000
2022-12-17 | 79400 | 79.4 | 7.34 | 7.54 | 125 | 19 | 340 | 44 | 279 | 24 | NA | 600 | 0.3 | 24.23 | 1300000
2022-12-18 | 82020 | 82.02 | 7.23 | 7.55 | 130 | 18 | 332 | 48 | 318 | 27 | NA | 400 | 0.2 | 23.26 | 1400000
2022-12-19 | 79610 | 79.61 | 7.25 | 7.54 | 125 | 17 | 348 | 44 | 310 | 26 | NA | 500 | 0.2 | 23.57 | 1700000
2022-12-20 | 79700 | 79.7 | 7.22 | 7.53 | 135 | 18 | 336 | 40 | 295 | 24 | NA | 600 | 0.3 | 24.47 | 1300000
2022-12-21 | 78090 | 78.09 | 7.29 | 7.52 | 140 | 17 | 328 | 44 | 285 | 26 | NA | 700 | 0.2 | 24.22 | 1700000
2022-12-22 | 73410 | 73.41 | 7.45 | 7.65 | 125 | 16 | 348 | 48 | 296 | 28 | NA | 600 | 0.3 | 23.47 | 1400000
2022-12-23 | 81530 | 81.53 | 7.36 | 7.6 | 145 | 19 | 344 | 44 | 308 | 26 | NA | 500 | 0.2 | 23.17 | 1300000
2022-12-24 | 80620 | 80.62 | 7.37 | 7.56 | 135 | 18 | 336 | 48 | 287 | 24 | NA | 400 | 0.2 | 23.65 | 1400000
2022-12-25 | 78690 | 78.69 | 7.39 | 7.55 | 140 | 17 | 324 | 40 | 295 | 27 | NA | 600 | 0.3 | 24.85 | 1700000
2022-12-26 | 79700 | 79.7 | 7.31 | 7.57 | 145 | 19 | 336 | 44 | 288 | 25 | NA | 500 | 0.2 | 23.3 | 1400000
2022-12-27 | 77580 | 77.58 | 7.27 | 7.58 | 135 | 16 | 324 | 40 | 298 | 26 | NA | 700 | 0.3 | 25.46 | 1700000
2022-12-28 | 82220 | 82.22 | 7.32 | 7.59 | 125 | 17 | 316 | 44 | 283 | 24 | NA | 600 | 0.2 | 24.03 | 1300000
2022-12-29 | 80640 | 80.64 | 7.31 | 7.55 | 130 | 18 | 312 | 40 | 279 | 25 | NA | 500 | 0.2 | 25.56 | 1400000
2022-12-30 | 76560 | 76.56 | 7.35 | 7.58 | 125 | 17 | 308 | 44 | 273 | 26 | NA | 400 | 0.3 | 22.41 | 1300000
2022-12-31 | 81310 | 81.31 | 7.3 | 7.57 | 140 | 18 | 312 | 48 | 286 | 27 | NA | 600 | 0.2 | 23.97 | 1700000
Average | 79434.5161 | 79.4323 | 7.3432 | 7.5952 | 133.0645 | 17.6129 | 328.6452 | 43.6129 | 290.5484 | 25.7419 | NA | 567.7419 | 0.23548 | 24.0465 | 1454838.7097
2462.4
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 73410 | 73.41 | 7.1 | 7.52 | 115 | 16 | 308 | 40 | 268 | 24 |  | 400 | 0.2 | 22.41 | 1300000
Max | 82220 | 82.22 | 7.6 | 7.76 | 150 | 19 | 348 | 48 | 318 | 29 |  | 700 | 0.3 | 25.56 | 1700000