## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-01 | 123880 | 123.88 | 7.26 | 7.32 | 120 | 28 | 328 | 40 | 302 | 35 | NA | 700 | 0.5 | 24.89 | 1400000
2023-02-02 | 117130 | 117.13 | 7.07 | 6.78 | 125 | 25 | 348 | 36 | 300 | 32 | NA | 600 | 0.4 | 24.57 | 1200000
2023-02-03 | 124710 | 124.71 | 7.64 | 7.31 | 140 | 28 | 356 | 41 | 312 | 36 | NA | 500 | 0.5 | 25.24 | 1700000
2023-02-04 | 121710 | 121.71 | 7.34 | 7.41 | 130 | 29 | 348 | 41 | 315 | 37 | NA | 800 | 0.5 | 24.13 | 1400000
2023-02-05 | 123310 | 123.31 | 7.9 | 7.43 | 145 | 28 | 356 | 42 | 311 | 39 | NA | 500 | 0.4 | 25.22 | 1700000
2023-02-06 | 120410 | 120.41 | 7.98 | 7.45 | 135 | 27 | 352 | 43 | 314 | 41 | NA | 400 | 0.5 | 24.85 | 1100000
2023-02-07 | 122520 | 122.52 | 7.44 | 7.41 | 130 | 26 | 340 | 40 | 312 | 36 | NA | 700 | 0.3 | 24.4 | 1300000
2023-02-08 | 121950 | 121.95 | 7.39 | 7.39 | 125 | 29 | 328 | 39 | 303 | 34 | NA | 500 | 0.2 | 25.1 | 1400000
2023-02-09 | 122540 | 122.54 | 7.36 | 7.35 | 130 | 28 | 332 | 44 | 305 | 42 | NA | 800 | 0.3 | 24.8 | 1700000
2023-02-10 | 123740 | 123.74 | 7.27 | 7.4 | 140 | 29 | 338 | 40 | 308 | 37 | NA | 700 | 0.2 | 25.07 | 1300000
2023-02-11 | 199620 | 119.62 | 7.32 | 7.45 | 145 | 28 | 344 | 42 | 313 | 39 | NA | 500 | 0.3 | 24.13 | 1400000
2023-02-12 | 119500 | 119.5 | 7.36 | 7.44 | 130 | 29 | 324 | 43 | 301 | 34 | NA | 600 | 0.2 | 25.1 | 1100000
2023-02-13 | 113200 | 113.2 | 7.39 | 7.48 | 125 | 30 | 322 | 46 | 305 | 39 | NA | 800 | 0.3 | 24.9 | 1200000
2023-02-14 | 113160 | 113.16 | 7.35 | 7.39 | 140 | 29 | 338 | 45 | 302 | 42 | NA | 600 | 0.3 | 25.1 | 1700000
2023-02-15 | 115340 | 115.34 | 7.41 | 7.47 | 135 | 28 | 329 | 42 | 308 | 37 | NA | 500 | 0.2 | 25.5 | 1400000
2023-02-16 | 115900 | 115.9 | 7.36 | 7.39 | 140 | 29 | 336 | 40 | 301 | 35 | NA | 700 | 0.2 | 25.2 | 1300000
2023-02-17 | 117500 | 117.5 | 7.38 | 7.45 | 130 | 28 | 348 | 44 | 304 | 41 | NA | 400 | 0.3 | 24.95 | 1700000
2023-02-18 | 117460 | 117.46 | 7.33 | 7.49 | 145 | 27 | 324 | 41 | 307 | 36 | NA | 600 | 0.2 | 25.09 | 1400000
2023-02-19 | 117940 | 117.94 | 7.28 | 7.43 | 125 | 28 | 332 | 43 | 310 | 40 | NA | 800 | 0.2 | 24.58 | 1200000
1900-02-19 | 116560 | 116.56 | 7.3 | 7.47 | 130 | 29 | 344 | 42 | 303 | 38 | NA | 500 | 0.3 | 25.14 | 1700000
2023-02-21 | 117590 | 117.59 | 7.41 | 7.54 | 120 | 27 | 335 | 40 | 308 | 36 | NA | 600 | 0.3 | 25.2 | 1400000
2023-02-22 | 118560 | 118.56 | 7.37 | 7.51 | 135 | 25 | 324 | 41 | 306 | 37 | NA | 700 | 0.2 | 24.81 | 1300000
2023-02-23 | 113980 | 113.98 | 7.35 | 7.49 | 140 | 28 | 338 | 43 | 310 | 39 | NA | 400 | 0.3 | 25.11 | 1700000
2023-02-24 | 114490 | 114.49 | 7.37 | 7.51 | 130 | 27 | 347 | 42 | 298 | 34 | NA | 600 | 0.2 | 24.6 | 1400000
2023-02-25 | 111490 | 111.49 | 7.38 | 7.56 | 120 | 28 | 252 | 41 | 300 | 37 | NA | 400 | 0.3 | 25.05 | 1200000
2023-02-26 | 113200 | 113.2 | 7.36 | 7.52 | 125 | 29 | 316 | 43 | 294 | 38 | NA | 700 | 0.2 | 24.86 | 1700000
2023-02-27 | 112890 | 112.89 | 7.47 | 7.57 | 135 | 30 | 339 | 46 | 303 | 42 | NA | 500 | 0.3 | 24.7 | 1400000
2023-02-28 | 112740 | 112.74 | 7.43 | 7.54 | 120 | 28 | 328 | 44 | 305 | 41 | NA | 600 | 0.3 | 25.3 | 1700000
Average | 120822.1429 | 117.965 | 7.4025 | 7.4268 | 131.7857 | 28 | 333.7857 | 41.9286 | 305.7143 | 37.6429 | NA | 596.4286 | 0.3 | 24.9139 | 1432142.8571
3303.02
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 111490 | 111.49 | 7.07 | 6.78 | 120 | 25 | 252 | 36 | 294 | 32 |  | 400 | 0.2 | 24.13 | 1100000
Max | 199620 | 124.71 | 7.98 | 7.57 | 145 | 30 | 356 | 46 | 315 | 42 |  | 800 | 0.5 | 25.5 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-01 | 81620 | 81.62 | 7.26 | 7.53 | 140 | 18 | 344 | 48 | 295 | 29 | NA | 600 | 0.3 | 23.41 | 1700000 | Nalla tapping of Rajapur SPS is closed at 5:16 PM on 07.01.2023 for taking more sewage from household network as per instructions given by UPJN. Also, retaining wall at tapping point is broken. Hence, raw sewage discharge from Rajapur SPS is less
2023-02-02 | 82320 | 82.32 | 7.28 | 7.52 | 130 | 17 | 324 | 44 | 307 | 28 | NA | 500 | 0.2 | 22.99 | 1400000
2023-02-03 | 78160 | 78.16 | 7.26 | 7.54 | 135 | 18 | 336 | 40 | 312 | 26 | NA | 700 | 0.3 | 26.15 | 1700000
2023-02-04 | 79030 | 79.03 | 7.32 | 7.5 | 130 | 17 | 316 | 44 | 305 | 27 | NA | 400 | 0.2 | 23.01 | 1400000
2023-02-05 | 78970 | 78.97 | 7.23 | 7.49 | 140 | 18 | 332 | 48 | 309 | 28 | NA | 600 | 0.3 | 23.27 | 1700000
2023-02-06 | 77660 | 77.66 | 7.25 | 7.48 | 125 | 17 | 328 | 40 | 286 | 26 | NA | 500 | 0.2 | 23.59 | 1300000
2023-02-07 | 77930 | 77.93 | 7.18 | 7.45 | 130 | 18 | 312 | 44 | 291 | 27 | NA | 700 | 0.3 | 23.73 | 1400000
2023-02-08 | 75060 | 75.06 | 7.21 | 7.44 | 135 | 17 | 336 | 40 | 311 | 26 | NA | 600 | 0.2 | 24.02 | 1700000
2023-02-09 | 78790 | 78.79 | 7.28 | 7.36 | 125 | 18 | 336 | 44 | 326 | 28 | NA | 500 | 0.2 | 24.17 | 1300000
2023-02-10 | 78960 | 78.96 | 7.33 | 7.45 | 130 | 17 | 312 | 40 | 304 | 26 | NA | 700 | 0.3 | 23.89 | 1700000
2023-02-11 | 77500 | 77.5 | 7.28 | 7.42 | 140 | 19 | 316 | 44 | 287 | 29 | NA | 400 | 0.2 | 23.79 | 1400000
2023-02-12 | 77870 | 77.87 | 7.26 | 7.5 | 135 | 18 | 324 | 48 | 305 | 30 | NA | 600 | 0.3 | 23.65 | 1700000
2023-02-13 | 74700 | 74.7 | 7.31 | 7.53 | 145 | 17 | 320 | 40 | 286 | 28 | NA | 700 | 0.2 | 26.78 | 1400000
2023-02-14 | 73490 | 73.49 | 7.25 | 7.55 | 130 | 16 | 328 | 44 | 298 | 27 | NA | 500 | 0.3 | 25.32 | 1700000
2023-02-15 | 80360 | 80.36 | 7.29 | 7.52 | 140 | 18 | 336 | 40 | 293 | 26 | NA | 600 | 0.3 | 23.62 | 1300000
2023-02-16 | 77530 | 77.53 | 7.28 | 7.51 | 130 | 19 | 324 | 44 | 279 | 25 | NA | 500 | 0.2 | 25.98 | 1400000
2023-02-17 | 83030 | 83.03 | 7.32 | 7.5 | 135 | 18 | 312 | 40 | 283 | 26 | NA | 400 | 0.3 | 22.98 | 1300000
2023-02-18 | 82910 | 82.91 | 7.24 | 7.49 | 145 | 19 | 324 | 44 | 286 | 25 | NA | 600 | 0.2 | 26.16 | 1700000
2023-02-19 | 79430 | 79.43 | 7.27 | 7.5 | 130 | 17 | 336 | 48 | 308 | 27 | NA | 700 | 0.3 | 23.13 | 1400000
1900-02-19 | 81960 | 81.96 | 7.24 | 7.49 | 135 | 16 | 328 | 44 | 297 | 28 | NA | 600 | 0.2 | 25.76 | 1300000
2023-02-21 | 79070 | 79.07 | 7.27 | 7.43 | 140 | 18 | 332 | 40 | 313 | 29 | NA | 500 | 0.3 | 24.47 | 1700000
2023-02-22 | 80870 | 80.87 | 7.29 | 7.51 | 135 | 17 | 324 | 44 | 297 | 26 | NA | 400 | 0.2 | 24.43 | 1400000
2023-02-23 | 72760 | 72.76 | 7.26 | 7.54 | 130 | 16 | 332 | 40 | 305 | 27 | NA | 600 | 0.3 | 23.69 | 1300000
2023-02-24 | 73840 | 73.84 | 7.31 | 7.57 | 140 | 17 | 328 | 44 | 295 | 25 | NA | 700 | 0.2 | 23.61 | 1700000
2023-02-25 | 80320 | 80.32 | 7.27 | 7.58 | 145 | 18 | 324 | 40 | 287 | 27 | NA | 600 | 0.3 | 24.39 | 1400000
2023-02-26 | 81760 | 81.76 | 7.23 | 7.57 | 130 | 17 | 316 | 44 | 293 | 26 | NA | 500 | 0.2 | 23.22 | 1700000
2023-02-27 | 76500 | 76.5 | 7.29 | 7.62 | 135 | 16 | 332 | 40 | 297 | 25 | NA | 700 | 0.3 | 23.72 | 1400000
2023-02-28 | 74830 | 74.83 | 7.33 | 7.55 | 140 | 18 | 336 | 44 | 310 | 26 | NA | 400 | 0.2 | 25.42 | 1300000
Average | 78472.5 | 78.4725 | 7.2711 | 7.505 | 135 | 17.4643 | 326.7143 | 43 | 298.75 | 26.8929 | NA | 564.2857 | 0.25 | 24.2268 | 1492857.1429
2197.23
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 72760 | 72.76 | 7.18 | 7.36 | 125 | 16 | 312 | 40 | 279 | 25 |  | 400 | 0.2 | 22.98 | 1300000
Max | 83030 | 83.03 | 7.33 | 7.62 | 145 | 19 | 344 | 48 | 326 | 30 |  | 700 | 0.3 | 26.78 | 1700000