## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-01-01 | 118940 | 118.94 | 7.33 | 7.41 | 140 | 26 | 344 | 41 | 306 | 28 | NA | 500 | 0.5 | 25.3 | 1300000
2023-01-02 | 107730 | 107.73 | 7.29 | 7.25 | 135 | 25 | 332 | 40 | 302 | 27 | NA | 700 | 0.4 | 25.02 | 1700000
2023-01-03 | 115720 | 115.62 | 7.33 | 7.35 | 140 | 27 | 340 | 42 | 308 | 26 | NA | 600 | 0.5 | 25.33 | 1200000
2023-01-04 | 115140 | 115.14 | 7.27 | 7.37 | 135 | 25 | 344 | 38 | 309 | 32 | NA | 800 | 0.4 | 25.31 | 1400000
2023-01-05 | 116780 | 116.78 | 7.33 | 7.26 | 130 | 27 | 336 | 40 | 306 | 34 | NA | 500 | 0.5 | 25.33 | 1300000
2023-01-06 | 117650 | 117.65 | 7.27 | 7.28 | 140 | 28 | 348 | 39 | 305 | 35 | NA | 800 | 0.4 | 24.9 | 1700000
2023-01-07 | 104830 | 104.83 | 7.33 | 7.29 | 145 | 27 | 352 | 41 | 309 | 38 | NA | 600 | 0.5 | 24.3 | 1400000
2023-01-08 | 103650 | 103.65 | 7.28 | 7.34 | 140 | 29 | 348 | 39 | 303 | 35 | NA | 700 | 0.4 | 24.5 | 1300000
2023-01-09 | 103680 | 103.68 | 7.31 | 7.41 | 135 | 28 | 356 | 41 | 307 | 36 | NA | 500 | 0.5 | 24.3 | 1700000
2023-01-10 | 105130 | 105.13 | 7.26 | 7.29 | 130 | 30 | 332 | 41 | 313 | 35 | NA | 800 | 0.4 | 24.68 | 1300000
2023-01-11 | 104670 | 104.67 | 7.29 | 7.27 | 125 | 29 | 324 | 45 | 311 | 38 | NA | 600 | 0.5 | 24.27 | 1400000
2023-01-12 | 105110 | 105.11 | 7.19 | 7.06 | 120 | 29 | 312 | 39 | 307 | 34 | NA | 400 | 0.5 | 25.2 | 1200000
2023-01-13 | 105130 | 105.13 | 7.24 | 7.01 | 135 | 27 | 320 | 41 | 290 | 37 | NA | 500 | 0.5 | 24.79 | 1300000
2023-01-14 | 108030 | 108.03 | 7.13 | 7.16 | 120 | 29 | 336 | 40 | 305 | 38 | NA | 700 | 0.4 | 24.52 | 1400000
2023-01-15 | 114270 | 114.27 | 7.28 | 7.47 | 130 | 28 | 348 | 39 | 306 | 36 | NA | 400 | 0.5 | 24.6 | 1700000
2023-01-16 | 110360 | 110.36 | 7.32 | 7.49 | 140 | 27 | 316 | 40 | 302 | 35 | NA | 600 | 0.4 | 25.23 | 1200000
2023-01-17 | 121680 | 121.68 | 7.11 | 7.06 | 135 | 26 | 336 | 43 | 305 | 29 | NA | 500 | 0.5 | 25.33 | 1400000
2023-01-18 | 119190 | 119.19 | 7.33 | 7.77 | 120 | 27 | 352 | 39 | 309 | 36 | NA | 700 | 0.4 | 25.2 | 1300000
2023-01-19 | 115830 | 115.83 | 7.28 | 7.72 | 125 | 28 | 320 | 40 | 301 | 35 | NA | 400 | 0.5 | 24.97 | 1700000
1900-01-19 | 118610 | 118.61 | 7.34 | 7.78 | 120 | 29 | 332 | 43 | 311 | 38 | NA | 800 | 0.4 | 25.12 | 1400000
2023-01-21 | 113280 | 113.28 | 7.32 | 7.75 | 140 | 28 | 348 | 42 | 314 | 38 | NA | 500 | 0.5 | 24.97 | 1700000
2023-01-22 | 117400 | 117.4 | 7.11 | 7.25 | 145 | 29 | 312 | 41 | 302 | 36 | NA | 700 | 0.4 | 25.08 | 1300000
2023-01-23 | 120470 | 120.47 | 7.32 | 7.27 | 140 | 27 | 328 | 40 | 306 | 37 | NA | 600 | 0.5 | 24.27 | 1400000
2023-01-24 | 120340 | 120.34 | 7.34 | 7.29 | 145 | 29 | 336 | 42 | 302 | 38 | NA | 800 | 0.4 | 24.6 | 1700000
2023-01-25 | 117600 | 117.6 | 7.19 | 7.32 | 130 | 27 | 340 | 41 | 305 | 37 | NA | 700 | 0.5 | 25.3 | 1400000
2023-01-26 | 118710 | 118.71 | 7.21 | 7.28 | 140 | 27 | 348 | 39 | 309 | 36 | NA | 500 | 0.3 | 25.3 | 1300000
2023-01-27 | 177070 | 117.07 | 7.18 | 7.3 | 130 | 29 | 340 | 40 | 313 | 35 | NA | 600 | 0.5 | 24.63 | 1200000
2023-01-28 | 188520 | 118.52 | 7.12 | 7.33 | 140 | 28 | 344 | 41 | 315 | 36 | NA | 800 | 0.4 | 25.17 | 1700000
2023-01-29 | 119790 | 119.79 | 7.26 | 7.31 | 120 | 26 | 352 | 43 | 305 | 38 | NA | 700 | 0.3 | 25.2 | 1300000
2023-01-30 | 122410 | 122.41 | 7.25 | 7.32 | 125 | 29 | 332 | 40 | 307 | 40 | NA | 600 | 0.5 | 25.12 | 1200000
2023-01-31 | 122730 | 122.73 | 7.34 | 7.3 | 130 | 27 | 340 | 43 | 310 | 37 | NA | 400 | 0.5 | 25.1 | 1700000
Average | 118401.6129 | 114.2048 | 7.2629 | 7.3471 | 133.0645 | 27.6452 | 337.0323 | 40.7419 | 306.5484 | 35.1613 | NA | 612.9032 | 0.44839 | 24.9335 | 1425806.4516
3540.35
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 103650 | 103.65 | 7.11 | 7.01 | 120 | 25 | 312 | 38 | 290 | 26 |  | 400 | 0.3 | 24.27 | 1200000
Max | 188520 | 122.73 | 7.34 | 7.78 | 145 | 30 | 356 | 45 | 315 | 40 |  | 800 | 0.5 | 25.33 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-01-01 | 76900 | 76.9 | 7.4 | 7.56 | 130 | 16 | 328 | 40 | 305 | 24 | NA | 400 | 0.2 | 23.23 | 1700000
2023-01-02 | 83600 | 83.6 | 7.39 | 7.61 | 135 | 17 | 312 | 44 | 286 | 26 | NA | 500 | 0.3 | 25.21 | 1400000
2023-01-03 | 75430 | 75.43 | 7.27 | 7.59 | 130 | 16 | 324 | 48 | 293 | 29 | NA | 700 | 0.2 | 23.47 | 1700000
2023-01-04 | 79330 | 79.33 | 7.33 | 7.6 | 125 | 19 | 316 | 44 | 278 | 25 | NA | 600 | 0.2 | 23.43 | 1300000
2023-01-05 | 77910 | 77.91 | 7.27 | 7.68 | 130 | 16 | 324 | 40 | 298 | 27 | NA | 400 | 0.3 | 24.03 | 1400000
2023-01-06 | 80070 | 80.07 | 7.3 | 7.69 | 125 | 18 | 308 | 44 | 292 | 24 | NA | 500 | 0.2 | 22.82 | 1700000
2023-01-07 | 78840 | 78.84 | 7.34 | 7.71 | 135 | 17 | 324 | 40 | 288 | 26 | NA | 700 | 0.2 | 23.98 | 1400000
2023-01-08 | 77560 | 77.56 | 7.37 | 7.67 | 130 | 18 | 332 | 44 | 307 | 28 | NA | 600 | 0.3 | 24.37 | 1400000
2023-01-09 | 75210 | 75.21 | 7.36 | 7.68 | 135 | 17 | 312 | 48 | 282 | 27 | NA | 400 | 0.2 | 24.45 | 1300000
2023-01-10 | 75750 | 75.75 | 7.32 | 7.69 | 130 | 16 | 336 | 44 | 304 | 27 | NA | 500 | 0.3 | 24.4 | 1700000
2023-01-11 | 77560 | 77.56 | 7.31 | 7.67 | 140 | 18 | 320 | 40 | 302 | 28 | NA | 600 | 0.2 | 23.06 | 1400000
2023-01-12 | 78580 | 78.58 | 7.41 | 7.68 | 135 | 17 | 328 | 44 | 298 | 27 | NA | 700 | 0.2 | 23.55 | 1300000
2023-01-13 | 81750 | 81.75 | 7.39 | 7.71 | 130 | 18 | 316 | 40 | 296 | 25 | NA | 500 | 0.3 | 23.81 | 1700000
2023-01-14 | 79990 | 79.99 | 7.36 | 7.67 | 140 | 19 | 320 | 44 | 301 | 26 | NA | 600 | 0.3 | 23.02 | 1400000
2023-01-15 | 79840 | 79.84 | 7.37 | 7.67 | 125 | 16 | 328 | 48 | 302 | 27 | NA | 500 | 0.2 | 24.37 | 1300000
2023-01-16 | 77260 | 77.26 | 7.27 | 7.68 | 140 | 18 | 324 | 44 | 294 | 29 | NA | 700 | 0.2 | 24.03 | 1700000
2023-01-17 | 79780 | 79.78 | 7.33 | 7.76 | 145 | 19 | 344 | 48 | 307 | 28 | NA | 600 | 0.3 | 25.76 | 1400000
2023-01-18 | 78560 | 78.56 | 7.41 | 7.74 | 135 | 17 | 312 | 40 | 278 | 25 | NA | 500 | 0.2 | 24.63 | 1700000
2023-01-19 | 79000 | 79 | 7.39 | 7.66 | 130 | 18 | 324 | 44 | 289 | 27 | NA | 400 | 0.2 | 23.77 | 1300000
2023-01-20 | 77020 | 77.02 | 7.38 | 7.69 | 125 | 19 | 336 | 48 | 302 | 29 | NA | 600 | 0.3 | 24.02 | 1700000
2023-01-21 | 88660 | 88.66 | 7.35 | 7.43 | 135 | 18 | 332 | 44 | 284 | 25 | NA | 500 | 0.2 | 22.25 | 1400000
2023-01-22 | 85290 | 85.29 | 7.28 | 7.64 | 145 | 19 | 344 | 48 | 315 | 29 | NA | 700 | 0.3 | 22.95 | 1700000
2023-01-23 | 80660 | 80.66 | 7.34 | 7.63 | 140 | 18 | 336 | 44 | 305 | 26 | NA | 600 | 0.2 | 23.99 | 1400000
2023-01-24 | 79280 | 79.28 | 7.32 | 7.6 | 135 | 17 | 316 | 48 | 297 | 26 | NA | 400 | 0.2 | 22.4 | 1300000
2023-01-25 | 84270 | 84.27 | 7.33 | 7.51 | 145 | 18 | 332 | 44 | 295 | 29 | NA | 500 | 0.2 | 25.72 | 1400000
2023-01-26 | 86550 | 86.55 | 7.39 | 7.44 | 140 | 19 | 324 | 48 | 283 | 28 | NA | 600 | 0.3 | 25.85 | 1700000
2023-01-27 | 84230 | 84.23 | 7.35 | 7.43 | 135 | 17 | 316 | 44 | 291 | 27 | NA | 700 | 0.2 | 22.23 | 1300000
2023-01-28 | 81540 | 81.54 | 7.29 | 7.48 | 125 | 18 | 328 | 40 | 288 | 26 | NA | 500 | 0.2 | 24.82 | 1400000
2023-01-29 | 80960 | 80.96 | 7.27 | 7.51 | 140 | 19 | 312 | 44 | 292 | 27 | NA | 600 | 0.3 | 23.97 | 1700000
2023-01-30 | 81230 | 81.23 | 7.25 | 7.57 | 145 | 18 | 332 | 48 | 307 | 28 | NA | 400 | 0.3 | 25.19 | 1300000
2023-01-31 | 84510 | 84.51 | 7.28 | 7.51 | 135 | 19 | 328 | 44 | 312 | 27 | NA | 700 | 0.2 | 25.55 | 1400000
Average | 80229.6774 | 80.2297 | 7.3361 | 7.6181 | 134.5161 | 17.7097 | 324.7742 | 44.2581 | 295.8387 | 26.8387 | NA | 554.8387 | 0.23871 | 24.0106 | 1480645.1613
2487.12
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 75210 | 75.21 | 7.25 | 7.43 | 125 | 16 | 308 | 40 | 278 | 24 |  | 400 | 0.2 | 22.23 | 1300000
Max | 88660 | 88.66 | 7.41 | 7.76 | 145 | 19 | 344 | 48 | 315 | 29 |  | 700 | 0.3 | 25.85 | 1700000