## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 104560 | 104.56 | 7.19 | 7.38 | 120 | 24 | 320 | 42 | 320 | 32 | NA | 500 | 0.3 | 24.11 | 1400000
2023-07-02 | 99950 | 99.95 | 7.23 | 7.39 | 130 | 26 | 296 | 40 | 274 | 30 | NA | 600 | 0.2 | 25 | 1300000
2023-07-03 | 104620 | 104.62 | 7.16 | 7.28 | 125 | 25 | 316 | 38 | 280 | 32 | NA | 800 | 0.3 | 25.01 | 1700000
2023-07-04 | 113920 | 113.92 | 7.11 | 7.31 | 120 | 23 | 324 | 40 | 310 | 31 | NA | 400 | 0.2 | 24.35 | 1100000
2023-07-05 | 110670 | 110.67 | 7.15 | 7.55 | 130 | 25 | 316 | 39 | 315 | 33 | NA | 800 | 0.3 | 25.07 | 1300000
2023-07-06 | 99930 | 99.93 | 7.29 | 7.43 | 125 | 26 | 318 | 36 | 290 | 30 | NA | 600 | 0.2 | 24.7 | 1400000
2023-07-07 | 97330 | 97.33 | 7.36 | 7.75 | 135 | 24 | 328 | 39 | 286 | 32 | NA | 700 | 0.3 | 24.8 | 1200000
2023-07-08 | 95370 | 95.37 | 7.25 | 7.61 | 120 | 23 | 312 | 38 | 280 | 30 | NA | 500 | 0.3 | 25.09 | 1300000
2023-07-09 | 99460 | 99.47 | 7.49 | 7.98 | 130 | 25 | 324 | 41 | 292 | 32 | NA | 400 | 0.2 | 24.9 | 1700000
2023-07-10 | 105390 | 105.39 | 7.33 | 7.41 | 120 | 22 | 320 | 38 | 304 | 31 | NA | 800 | 0.2 | 24.78 | 1100000
2023-07-11 | 95890 | 95.89 | 7.19 | 7.58 | 140 | 23 | 318 | 37 | 290 | 32 | NA | 600 | 0.3 | 25 | 1400000
2023-07-12 | 98790 | 98.79 | 7.23 | 7.76 | 135 | 25 | 332 | 40 | 296 | 30 | NA | 500 | 0.2 | 23.51 | 1300000
2023-07-13 | 101280 | 101.28 | 7.33 | 7.44 | 140 | 24 | 344 | 36 | 303 | 28 | NA | 700 | 0.3 | 24.9 | 1700000
2023-07-14 | 108470 | 108.47 | 7.16 | 7.75 | 130 | 23 | 324 | 40 | 294 | 29 | NA | 800 | 0.3 | 25.3 | 1400000
2023-07-15 | 106040 | 106.04 | 7.18 | 7.67 | 135 | 25 | 312 | 36 | 281 | 30 | NA | 400 | 0.2 | 24.36 | 1200000
2023-07-16 | 109120 | 109.12 | 7.29 | 7.27 | 120 | 23 | 318 | 37 | 296 | 28 | NA | 600 | 0.3 | 24.7 | 1300000
2023-07-17 | 105440 | 105.44 | 7.18 | 7.33 | 125 | 24 | 324 | 39 | 301 | 32 | NA | 500 | 0.2 | 24.9 | 1400000
2023-07-18 | 99960 | 99.96 | 7.16 | 7.27 | 130 | 28 | 310 | 38 | 290 | 31 | NA | 700 | 0.2 | 23.8 | 1700000
2023-07-19 | 99350 | 99.35 | 7.15 | 7.26 | 140 | 25 | 316 | 40 | 284 | 33 | NA | 800 | 0.3 | 24.3 | 1100000
2023-07-20 | 105210 | 105.21 | 7.13 | 7.33 | 130 | 21 | 320 | 38 | 305 | 32 | NA | 400 | 0.2 | 24.7 | 1300000
2023-07-21 | 101890 | 101.89 | 7.16 | 7.29 | 140 | 23 | 328 | 39 | 301 | 30 | NA | 700 | 0.3 | 25.08 | 1200000
2023-07-22 | 103080 | 103.08 | 7.19 | 7.31 | 120 | 22 | 312 | 38 | 276 | 29 | NA | 500 | 0.3 | 24.15 | 1400000
2023-07-23 | 109020 | 109.02 | 7.18 | 7.29 | 140 | 25 | 341 | 40 | 303 | 31 | NA | 600 | 0.2 | 24.94 | 1700000
2023-07-24 | 101930 | 101.93 | 7.21 | 7.35 | 120 | 26 | 312 | 42 | 298 | 30 | NA | 800 | 0.3 | 24.92 | 1200000
2023-07-25 | 106290 | 106.29 | 7.28 | 7.39 | 125 | 25 | 296 | 40 | 284 | 32 | NA | 700 | 0.2 | 24.7 | 1700000
2023-07-26 | 103810 | 103.81 | 7.24 | 7.34 | 120 | 22 | 304 | 38 | 303 | 31 | NA | 400 | 0.3 | 24.8 | 1100000
2023-07-27 | 107160 | 107.16 | 7.25 | 7.36 | 130 | 25 | 292 | 40 | 296 | 30 | NA | 600 | 0.2 | 24.7 | 1400000
2023-07-28 | 98540 | 98.54 | 7.24 | 7.35 | 125 | 28 | 308 | 41 | 302 | 29 | NA | 500 | 0.2 | 24.75 | 1300000
2023-07-29 | 113970 | 113.97 | 7.27 | 7.31 | 130 | 25 | 312 | 40 | 280 | 30 | NA | 800 | 0.3 | 24.5 | 1200000
2023-07-30 | 91510 | 91.51 | 7.29 | 7.41 | 120 | 23 | 294 | 38 | 283 | 29 | NA | 600 | 0.2 | 21 | 1100000
2023-07-31 | 103760 | 103.76 | 7.27 | 7.45 | 125 | 22 | 316 | 36 | 281 | 28 | NA | 500 | 0.3 | 24.66 | 1300000
Average | 103280.9677 | 103.2813 | 7.2303 | 7.4387 | 128.2258 | 24.1935 | 316.3548 | 38.8387 | 293.4839 | 30.5484 | NA | 606.4516 | 0.25161 | 24.5639 | 1351612.9032
3201.72
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 91510 | 91.51 | 7.11 | 7.26 | 120 | 21 | 292 | 36 | 274 | 28 |  | 400 | 0.2 | 21 | 1100000
Max | 113970 | 113.97 | 7.49 | 7.98 | 140 | 28 | 344 | 42 | 320 | 33 |  | 800 | 0.3 | 25.3 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 83750 | 83.75 | 7.22 | 7.46 | 125 | 16 | 316 | 40 | 279 | 25 | NA | 700 | 0.3 | 22.26 | 1300000
2023-07-02 | 81350 | 81.35 | 7.35 | 7.63 | 135 | 17 | 304 | 40 | 272 | 26 | NA | 600 | 0.2 | 22.71 | 1200000
2023-07-03 | 76210 | 76.21 | 7.36 | 7.68 | 120 | 16 | 312 | 44 | 268 | 27 | NA | 500 | 0.3 | 23.65 | 1400000
2023-07-04 | 84410 | 84.41 | 7.17 | 7.69 | 130 | 17 | 304 | 40 | 261 | 26 | NA | 400 | 0.2 | 24.92 | 1300000
2023-07-05 | 83380 | 83.38 | 7.28 | 7.59 | 125 | 16 | 312 | 42 | 271 | 25 | NA | 600 | 0.3 | 23.75 | 1700000
2023-07-06 | 76650 | 76.65 | 7.15 | 7.61 | 130 | 17 | 308 | 44 | 257 | 26 | NA | 500 | 0.3 | 22.83 | 1300000
2023-07-07 | 79670 | 79.67 | 7.18 | 7.67 | 135 | 18 | 316 | 44 | 268 | 27 | NA | 400 | 0.2 | 23.42 | 1400000
2023-07-08 | 76250 | 76.25 | 7.16 | 7.64 | 125 | 16 | 320 | 40 | 265 | 28 | NA | 700 | 0.3 | 23.71 | 1700000
2023-07-09 | 82050 | 82.05 | 7.18 | 7.65 | 130 | 17 | 304 | 44 | 257 | 27 | NA | 600 | 0.3 | 23.75 | 1300000
2023-07-10 | 85030 | 85.03 | 7.11 | 7.54 | 135 | 18 | 296 | 40 | 247 | 28 | NA | 500 | 0.2 | 22.8 | 1400000
2023-07-11 | 83040 | 83.04 | 7.17 | 7.55 | 120 | 15 | 292 | 36 | 243 | 26 | NA | 400 | 0.3 | 23.18 | 1200000
2023-07-12 | 81170 | 81.17 | 7.14 | 7.63 | 125 | 16 | 304 | 40 | 257 | 27 | NA | 600 | 0.2 | 24.56 | 1700000
2023-07-13 | 78120 | 78.12 | 7.06 | 7.65 | 130 | 15 | 308 | 44 | 249 | 26 | NA | 500 | 0.3 | 23.03 | 1300000
2023-07-14 | 81940 | 81.94 | 7.05 | 7.69 | 135 | 17 | 292 | 40 | 259 | 27 | NA | 600 | 0.3 | 23.18 | 1400000
2023-07-15 | 78020 | 78.02 | 7.03 | 7.68 | 125 | 16 | 304 | 44 | 261 | 28 | NA | 400 | 0.2 | 23.54 | 1700000
2023-07-16 | 81120 | 81.12 | 7.09 | 7.67 | 130 | 17 | 324 | 40 | 295 | 27 | NA | 500 | 0.3 | 23.11 | 1300000
2023-07-17 | 79520 | 79.52 | 7.03 | 7.62 | 125 | 16 | 340 | 40 | 273 | 27 | NA | 600 | 0.3 | 24.8 | 1700000
2023-07-18 | 79230 | 79.23 | 7.08 | 7.69 | 120 | 15 | 336 | 44 | 285 | 28 | NA | 400 | 0.2 | 24.9 | 1200000
2023-07-19 | 80830 | 80.83 | 7.09 | 7.7 | 130 | 16 | 328 | 40 | 289 | 27 | NA | 600 | 0.3 | 24.56 | 1400000
2023-07-20 | 78840 | 78.84 | 7.12 | 7.69 | 125 | 15 | 324 | 40 | 292 | 28 | NA | 500 | 0.3 | 23.22 | 1700000
2023-07-21 | 79340 | 79.34 | 7.03 | 7.65 | 135 | 17 | 320 | 44 | 278 | 25 | NA | 700 | 0.3 | 23.37 | 1400000
2023-07-22 | 71270 | 71.27 | 7.06 | 7.71 | 130 | 16 | 328 | 40 | 276 | 24 | NA | 400 | 0.2 | 23.33 | 1300000
2023-07-23 | 84950 | 84.95 | 7.11 | 7.64 | 125 | 17 | 316 | 44 | 272 | 25 | NA | 600 | 0.3 | 22.85 | 1700000
2023-07-24 | 77530 | 77.53 | 7.18 | 7.67 | 130 | 16 | 304 | 40 | 269 | 24 | NA | 500 | 0.3 | 24.79 | 1200000
2023-07-25 | 78210 | 78.21 | 7.21 | 7.69 | 120 | 17 | 316 | 44 | 284 | 25 | NA | 700 | 0.2 | 24.97 | 1400000
2023-07-26 | 79690 | 79.69 | 7.17 | 7.71 | 135 | 18 | 336 | 48 | 295 | 26 | NA | 600 | 0.3 | 24.64 | 1300000
2023-07-27 | 75100 | 75.1 | 7.28 | 7.72 | 125 | 16 | 292 | 44 | 266 | 24 | NA | 700 | 0.2 | 23.25 | 1400000
2023-07-28 | 79130 | 79.13 | 7.31 | 7.62 | 135 | 18 | 324 | 45 | 298 | 25 | NA | 500 | 0.3 | 24.3 | 1700000
2023-07-29 | 83650 | 83.65 | 7.33 | 7.61 | 120 | 16 | 308 | 40 | 279 | 26 | NA | 400 | 0.2 | 22.39 | 1300000
2023-07-30 | 79150 | 79.15 | 7.34 | 7.59 | 125 | 17 | 312 | 44 | 282 | 25 | NA | 600 | 0.2 | 23.33 | 1400000
2023-07-31 | 82510 | 82.51 | 7.32 | 7.6 | 120 | 16 | 304 | 40 | 274 | 24 | NA | 500 | 0.3 | 23.55 | 1300000
Average | 80035.8065 | 80.0358 | 7.1729 | 7.6432 | 127.5806 | 16.4516 | 313.0323 | 41.9032 | 271.6452 | 26.0968 | NA | 541.9355 | 0.26129 | 23.6339 | 1419354.8387
| 2481110 | 2481.11
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 71270 | 71.27 | 7.03 | 7.46 | 120 | 15 | 292 | 36 | 243 | 24 |  | 400 | 0.2 | 22.26 | 1200000
Max | 85030 | 85.03 | 7.36 | 7.72 | 135 | 18 | 340 | 48 | 298 | 28 |  | 700 | 0.3 | 24.97 | 1700000