## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-07-01 | 124400 | 124.4 | 7.29 | 7.36 | 136 | 20 | 344 | 40 | 306 | 30 | NA | 500 | 0.2 | 25.2 | 1400000
2022-07-02 | 123060 | 123.06 | 7.31 | 7.36 | 129 | 18 | 336 | 44 | 298 | 32 | NA | 400 | 0.2 | 25.4 | 1200000
2022-07-03 | 123300 | 123.3 | 7.32 | 7.39 | 133 | 20 | 340 | 40 | 296 | 33 | NA | 600 | 0.3 | 25.2 | 1300000
2022-07-04 | 126100 | 126.1 | 7.29 | 7.36 | 139 | 23 | 344 | 48 | 301 | 34 | NA | 700 | 0.2 | 25.2 | 1700000
2022-07-05 | 122650 | 122.65 | 7.33 | 7.35 | 139 | 20 | 352 | 40 | 303 | 32 | NA | 500 | 0.2 | 25.3 | 1200000
2022-07-06 | 123690 | 123.69 | 7.29 | 7.36 | 133 | 22 | 340 | 44 | 306 | 34 | NA | 600 | 0.2 | 25.2 | 1400000
2022-07-07 | 122800 | 122.8 | 7.32 | 7.41 | 129 | 18 | 328 | 36 | 308 | 32 | NA | 400 | 0.2 | 25.3 | 1700000
2022-07-08 | 127140 | 127.14 | 7.28 | 7.36 | 136 | 20 | 344 | 40 | 298 | 30 | NA | 700 | 0.3 | 25.2 | 1300000
2022-07-09 | 126600 | 126.6 | 7.33 | 7.39 | 133 | 22 | 340 | 48 | 303 | 33 | NA | 500 | 0.2 | 25.3 | 1200000
2022-07-10 | 133900 | 133.9 | 7.35 | 7.37 | 129 | 19 | 332 | 40 | 305 | 30 | NA | 600 | 0.2 | 25.1 | 1100000
2022-07-11 | 122590 | 122.59 | 7.34 | 7.39 | 136 | 21 | 348 | 44 | 308 | 32 | NA | 700 | 0.2 | 25.6 | 1300000
2022-07-12 | 122400 | 122.4 | 7.29 | 7.41 | 129 | 20 | 336 | 40 | 296 | 34 | NA | 400 | 0.2 | 25.6 | 1400000
2022-07-13 | 118310 | 118.31 | 7.31 | 7.38 | 139 | 23 | 348 | 48 | 298 | 35 | NA | 500 | 0.3 | 25.3 | 1700000
2022-07-14 | 119160 | 119.16 | 7.33 | 7.41 | 129 | 20 | 336 | 40 | 301 | 33 | NA | 600 | 0.3 | 25.1 | 1200000
2022-07-15 | 122700 | 122.7 | 7.31 | 7.36 | 136 | 24 | 344 | 48 | 305 | 30 | NA | 700 | 0.3 | 25.5 | 1100000
2022-07-16 | 105940 | 105.94 | 7.28 | 7.34 | 133 | 22 | 340 | 40 | 299 | 32 | NA | 600 | 0.2 | 25.4 | 1300000
2022-07-17 | 103950 | 103.95 | 7.33 | 7.36 | 129 | 21 | 332 | 44 | 305 | 29 | NA | 500 | 0.3 | 23.8 | 1200000
2022-07-18 | 116060 | 116.06 | 7.28 | 7.35 | 136 | 22 | 348 | 36 | 302 | 31 | NA | 400 | 0.2 | 23.3 | 1100000
2022-07-19 | 118700 | 118.7 | 7.29 | 7.36 | 139 | 20 | 340 | 40 | 297 | 33 | NA | 600 | 0.3 | 25.4 | 1400000
2022-07-20 | 122630 | 122.63 | 7.33 | 7.37 | 129 | 21 | 332 | 44 | 306 | 32 | NA | 400 | 0.3 | 25.5 | 1100000
2022-07-21 | 124390 | 124.39 | 7.29 | 7.35 | 136 | 23 | 344 | 48 | 308 | 35 | NA | 700 | 0.2 | 25.4 | 1300000
2022-07-22 | 124410 | 124.41 | 7.33 | 7.37 | 133 | 20 | 336 | 40 | 305 | 31 | NA | 400 | 0.3 | 25.5 | 1100000
2022-07-23 | 131210 | 131.21 | 7.28 | 7.36 | 139 | 21 | 348 | 44 | 308 | 32 | NA | 500 | 0.2 | 25.3 | 1200000
2022-07-24 | 125820 | 125.82 | 7.29 | 7.28 | 129 | 20 | 328 | 40 | 305 | 34 | NA | 600 | 0.3 | 25.6 | 1700000
2022-07-25 | 110020 | 110.02 | 7.32 | 7.35 | 133 | 22 | 332 | 44 | 298 | 33 | NA | 700 | 0.3 | 25.5 | 1400000
2022-07-26 | 108020 | 108.02 | 7.28 | 7.33 | 139 | 24 | 340 | 48 | 302 | 30 | NA | 800 | 0.3 | 24.8 | 1700000
2022-07-27 | 109210 | 109.21 | 7.31 | 7.41 | 136 | 20 | 348 | 40 | 305 | 32 | NA | 700 | 0.2 | 25.4 | 1100000
2022-07-28 | 100020 | 100.02 | 7.29 | 7.36 | 129 | 19 | 336 | 44 | 302 | 34 | NA | 600 | 0.2 | 25 | 1400000
2022-07-29 | 103280 | 103.28 | 7.33 | 7.39 | 126 | 20 | 328 | 40 | 307 | 31 | NA | 500 | 0.3 | 25.5 | 1300000
2022-07-30 | 100700 | 100.7 | 7.28 | 7.34 | 128 | 22 | 340 | 48 | 305 | 33 | NA | 700 | 0.3 | 25.3 | 1200000
2022-07-31 | 110410 | 110.41 | 7.33 | 7.36 | 123 | 20 | 332 | 40 | 301 | 30 | NA | 800 | 0.3 | 25.5 | 1700000
Average | 118502.2581 | 118.5023 | 7.3074 | 7.3658 | 132.9677 | 20.871 | 339.2258 | 42.5806 | 302.8065 | 32.129 | NA | 577.4194 | 0.24839 | 25.2161 | 1335483.871
3673.57
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 100020 | 100.02 | 7.28 | 7.28 | 123 | 18 | 328 | 36 | 296 | 29 |  | 400 | 0.2 | 23.3 | 1100000
Max | 133900 | 133.9 | 7.35 | 7.41 | 139 | 24 | 352 | 48 | 308 | 35 |  | 800 | 0.3 | 25.6 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-07-01 | 94460 | 94.46 | 7.39 | 7.68 | 145 | 18 | 344 | 40 | 312 | 27 | NA | 400 | 0.2 | 21.87 | 1400000
2022-07-02 | 95210 | 95.21 | 7.36 | 7.72 | 140 | 16 | 340 | 36 | 287 | 24 | NA | 500 | 0.3 | 22.85 | 1700000
2022-07-03 | 88740 | 88.74 | 7.41 | 7.67 | 135 | 17 | 328 | 44 | 293 | 28 | NA | 600 | 0.2 | 22.39 | 1400000
2022-07-04 | 85760 | 85.76 | 7.43 | 7.71 | 130 | 16 | 332 | 40 | 298 | 25 | NA | 400 | 0.3 | 23.57 | 1300000
2022-07-05 | 88650 | 88.65 | 7.35 | 7.68 | 125 | 15 | 324 | 36 | 276 | 23 | NA | 700 | 0.4 | 24.15 | 1700000
2022-07-06 | 89510 | 89.51 | 7.38 | 7.69 | 135 | 17 | 336 | 40 | 285 | 26 | NA | 500 | 0.3 | 23.27 | 1400000
2022-07-07 | 89160 | 89.16 | 7.42 | 7.65 | 130 | 18 | 320 | 44 | 307 | 28 | NA | 600 | 0.2 | 24.53 | 1700000
2022-07-08 | 88870 | 88.87 | 7.37 | 7.71 | 125 | 16 | 328 | 40 | 298 | 27 | NA | 500 | 0.2 | 23.67 | 1300000
2022-07-09 | 90580 | 90.58 | 7.43 | 7.67 | 135 | 17 | 344 | 44 | 312 | 25 | NA | 400 | 0.3 | 22.98 | 1700000
2022-07-10 | 93640 | 93.64 | 7.39 | 7.72 | 130 | 16 | 348 | 48 | 295 | 29 | NA | 600 | 0.2 | 23.35 | 1400000
2022-07-11 | 89400 | 89.4 | 7.45 | 7.7 | 125 | 18 | 332 | 40 | 305 | 26 | NA | 500 | 0.3 | 24.63 | 1200000
2022-07-12 | 84340 | 84.34 | 7.36 | 7.69 | 135 | 17 | 328 | 44 | 293 | 28 | NA | 600 | 0.2 | 23.57 | 1100000
2022-07-13 | 83830 | 83.83 | 7.41 | 7.72 | 130 | 16 | 320 | 36 | 279 | 25 | NA | 400 | 0.3 | 22.86 | 1400000
2022-07-14 | 80920 | 80.92 | 7.42 | 7.68 | 125 | 18 | 336 | 40 | 298 | 29 | NA | 500 | 0.4 | 23.39 | 1300000
2022-07-15 | 85440 | 85.44 | 7.39 | 7.58 | 140 | 17 | 324 | 36 | 312 | 28 | NA | 600 | 0.2 | 24.53 | 1200000
2022-07-16 | 88030 | 88.03 | 7.38 | 7.67 | 145 | 19 | 332 | 44 | 295 | 26 | NA | 400 | 0.2 | 23.67 | 1400000
2022-07-17 | 86560 | 86.56 | 7.35 | 7.72 | 135 | 18 | 340 | 48 | 287 | 28 | NA | 500 | 0.3 | 22.45 | 1700000
2022-07-18 | 87430 | 87.43 | 7.43 | 7.68 | 130 | 17 | 328 | 40 | 312 | 25 | NA | 600 | 0.2 | 23.35 | 1300000
2022-07-19 | 86030 | 86.03 | 7.38 | 7.7 | 125 | 16 | 344 | 36 | 293 | 29 | NA | 500 | 0.2 | 24.15 | 1400000
2022-07-20 | 86010 | 86.01 | 7.45 | 7.69 | 140 | 18 | 332 | 44 | 305 | 27 | NA | 400 | 0.3 | 22.98 | 1200000
2022-07-21 | 88510 | 88.51 | 7.41 | 7.66 | 125 | 17 | 336 | 40 | 295 | 26 | NA | 600 | 0.2 | 23.35 | 1700000
2022-07-22 | 92060 | 92.06 | 7.39 | 7.71 | 130 | 18 | 324 | 44 | 307 | 28 | NA | 500 | 0.3 | 23.57 | 1400000
2022-07-23 | 63350 | 63.35 | 7.37 | 7.69 | 125 | 16 | 328 | 36 | 289 | 25 | NA | 700 | 0.2 | 23.73 | 1300000 | Mumfordganj SPS was shutdown at 1:45 PM on 23.07.2022 due to installation of scour valve in rising main form Mumfordganj SPS to Rajapur STP by MORTH department.
2022-07-24 | 73490 | 73.49 | 7.42 | 7.72 | 135 | 18 | 332 | 40 | 291 | 27 | NA | 500 | 0.2 | 22.62 | 1200000 | Mumfordganj SPS was strated at 2:00 PM on 24.07.2022 after completion of installation work of scour valve in rising main form Mumfordganj SPS to Rajapur STP by MORTH department.
2022-07-25 | 96160 | 96.16 | 7.35 | 7.63 | 130 | 19 | 340 | 44 | 310 | 29 | NA | 400 | 0.3 | 24.37 | 1400000
2022-07-26 | 94070 | 94.07 | 7.38 | 7.65 | 125 | 17 | 344 | 40 | 297 | 26 | NA | 500 | 0.2 | 24.65 | 1700000
2022-07-27 | 87030 | 87.03 | 7.36 | 7.62 | 135 | 16 | 336 | 36 | 309 | 25 | NA | 600 | 0.2 | 23.78 | 1400000
2022-07-28 | 84650 | 84.65 | 7.39 | 7.63 | 125 | 18 | 328 | 40 | 285 | 27 | NA | 400 | 0.2 | 22.52 | 1200000
2022-07-29 | 80250 | 80.25 | 7.35 | 7.61 | 135 | 19 | 324 | 36 | 297 | 29 | NA | 600 | 0.3 | 22.8 | 1700000
2022-07-30 | 70420 | 70.42 | 7.41 | 7.73 | 130 | 17 | 332 | 44 | 287 | 28 | NA | 500 | 0.2 | 23.37 | 1300000 | Raw sewage received at Rajapur STP is less than normal as puming from Mumfordganj SPS was low due to less raw sewage received from Alopibagh SPS
2022-07-31 | 66400 | 66.4 | 7.38 | 7.69 | 125 | 18 | 328 | 40 | 279 | 24 | NA | 400 | 0.3 | 25.79 | 1200000
Average | 85772.9032 | 85.7729 | 7.3923 | 7.6797 | 131.6129 | 17.1935 | 332.6452 | 40.6452 | 296.3871 | 26.6774 | NA | 512.9032 | 0.25161 | 23.5084 | 1409677.4194
2658.96
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 63350 | 63.35 | 7.35 | 7.58 | 125 | 15 | 320 | 36 | 276 | 23 |  | 400 | 0.2 | 21.87 | 1100000
Max | 96160 | 96.16 | 7.45 | 7.73 | 145 | 19 | 348 | 48 | 312 | 29 |  | 700 | 0.4 | 25.79 | 1700000