## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-06-01 | 119770 | 119.77 | 7.28 | 7.35 | 129 | 18 | 336 | 36 | 307 | 28 | NA | 500 | 0.3 | 25.1 | 1300000
2022-06-02 | 118110 | 118.11 | 7.33 | 7.36 | 136 | 20 | 344 | 40 | 309 | 29 | NA | 700 | 0.2 | 25.7 | 1700000
2022-06-03 | 119240 | 119.24 | 7.34 | 7.44 | 133 | 22 | 336 | 44 | 302 | 30 | NA | 400 | 0.2 | 25.5 | 1400000
2022-06-04 | 118120 | 118.12 | 7.33 | 7.41 | 129 | 20 | 328 | 48 | 307 | 28 | NA | 600 | 0.3 | 25.6 | 1200000
2022-06-05 | 127910 | 127.91 | 7.28 | 7.36 | 136 | 18 | 340 | 40 | 304 | 31 | NA | 700 | 0.2 | 25.1 | 1100000
2022-06-06 | 116110 | 116.11 | 7.26 | 7.35 | 129 | 17 | 332 | 36 | 309 | 29 | NA | 500 | 0.2 | 25.4 | 1300000
2022-06-07 | 109460 | 109.46 | 7.32 | 7.38 | 139 | 19 | 348 | 44 | 314 | 32 | NA | 600 | 0.3 | 25 | 1400000
2022-06-08 | 124990 | 124.99 | 7.31 | 7.35 | 133 | 20 | 340 | 40 | 303 | 28 | NA | 400 | 0.2 | 25.3 | 1200000
2022-06-09 | 116760 | 116.76 | 7.29 | 7.36 | 129 | 23 | 328 | 48 | 298 | 29 | NA | 700 | 0.2 | 25.1 | 1700000
2022-06-10 | 116140 | 116.14 | 7.33 | 7.39 | 136 | 21 | 340 | 40 | 305 | 31 | NA | 400 | 0.3 | 25.3 | 1100000
2022-06-11 | 112810 | 112.81 | 7.28 | 7.35 | 129 | 19 | 328 | 44 | 302 | 32 | NA | 600 | 0.2 | 25.2 | 1400000
2022-06-12 | 116500 | 116.5 | 7.31 | 7.38 | 133 | 20 | 340 | 40 | 309 | 34 | NA | 500 | 0.3 | 25.5 | 1300000
2022-06-13 | 127710 | 127.71 | 7.28 | 7.33 | 136 | 23 | 332 | 48 | 314 | 30 | NA | 700 | 0.2 | 25.2 | 1200000
2022-06-14 | 108220 | 108.22 | 7.33 | 7.39 | 139 | 21 | 340 | 40 | 308 | 28 | NA | 600 | 0.3 | 24.9 | 1700000
2022-06-15 | 125940 | 125.94 | 7.28 | 7.36 | 133 | 22 | 348 | 44 | 305 | 30 | NA | 400 | 0.2 | 25.6 | 1100000
2022-06-16 | 121980 | 121.98 | 7.33 | 7.38 | 129 | 18 | 332 | 36 | 309 | 28 | NA | 500 | 0.3 | 25.4 | 1400000
2022-06-17 | 114250 | 114.25 | 7.32 | 7.35 | 133 | 20 | 340 | 40 | 304 | 31 | NA | 700 | 0.2 | 25.8 | 1300000
2022-06-18 | 114860 | 114.86 | 7.31 | 7.37 | 136 | 21 | 328 | 44 | 307 | 32 | NA | 500 | 0.2 | 25.3 | 1200000
2022-06-19 | 115600 | 115.6 | 7.33 | 7.39 | 129 | 18 | 344 | 36 | 298 | 33 | NA | 600 | 0.2 | 25.2 | 1400000
2022-06-20 | 132330 | 132.33 | 7.29 | 7.36 | 129 | 20 | 328 | 40 | 297 | 34 | NA | 400 | 0.3 | 24.6 | 1700000
2022-06-21 | 125470 | 125.47 | 7.32 | 7.37 | 133 | 22 | 332 | 48 | 303 | 36 | NA | 700 | 0.3 | 26 | 1300000
2022-06-22 | 118330 | 118.33 | 7.29 | 7.39 | 136 | 20 | 340 | 40 | 307 | 33 | NA | 500 | 0.2 | 25.9 | 1200000
2022-06-23 | 126070 | 126.07 | 7.31 | 7.38 | 139 | 19 | 348 | 44 | 306 | 31 | NA | 600 | 0.2 | 25.3 | 1100000
2022-06-24 | 119690 | 119.69 | 7.29 | 7.37 | 129 | 20 | 336 | 40 | 309 | 34 | NA | 400 | 0.3 | 25.2 | 1300000
2022-06-25 | 128430 | 128.43 | 7.33 | 7.36 | 136 | 22 | 340 | 48 | 303 | 32 | NA | 700 | 0.2 | 25.6 | 1400000
2022-06-26 | 118510 | 118.51 | 7.29 | 7.34 | 129 | 19 | 332 | 40 | 309 | 30 | NA | 700 | 0.3 | 25.6 | 1700000
2022-06-27 | 106960 | 106.96 | 7.32 | 7.39 | 133 | 20 | 340 | 44 | 306 | 29 | NA | 500 | 0.3 | 25.9 | 1200000 | Raw sewage received is less as Chacharnalla pumping station was shutdown on 27th June 2022 for rectification of leakage in header line hence at Gaughat MPS, only one pump was in operation.
2022-06-28 | 81500 | 81.5 | 7.29 | 7.33 | 129 | 22 | 328 | 36 | 298 | 31 | NA | 600 | 0.3 | 25.6 | 1400000
2022-06-29 | 86100 | 86.1 | 7.33 | 7.36 | 136 | 20 | 340 | 40 | 303 | 32 | NA | 700 | 0.2 | 25.2 | 1300000
2022-06-30 | 126780 | 126.78 | 7.29 | 7.34 | 129 | 18 | 328 | 36 | 302 | 29 | NA | 400 | 0.2 | 25.3 | 1100000 | Raw sewage received is normal as Chacharnalla SPS was taken in operation on 30th June 2022 after completion of maintenance work hence Gaughat MPS was also running at full capacity.
Average | 117155 | 117.155 | 7.3063 | 7.368 | 132.8 | 20.0667 | 336.5333 | 41.4667 | 305.2333 | 30.8 | NA | 560 | 0.24333 | 25.38 | 1336666.6667
3514.65
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 81500 | 81.5 | 7.26 | 7.33 | 129 | 17 | 328 | 36 | 297 | 28 |  | 400 | 0.2 | 24.6 | 1100000
Max | 132330 | 132.33 | 7.34 | 7.44 | 139 | 23 | 348 | 48 | 314 | 36 |  | 700 | 0.3 | 26 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-06-01 | 79330 | 79.33 | 7.38 | 7.58 | 125 | 15 | 332 | 36 | 296 | 25 | NA | 500 | 0.2 | 21.83 | 1700000
2022-06-02 | 80160 | 80.16 | 7.41 | 7.63 | 135 | 18 | 340 | 44 | 287 | 27 | NA | 600 | 0.2 | 22.73 | 1400000
2022-06-03 | 80910 | 80.91 | 7.37 | 7.65 | 130 | 16 | 336 | 40 | 285 | 24 | NA | 400 | 0.3 | 21.49 | 1300000
2022-06-04 | 83320 | 83.32 | 7.43 | 7.72 | 125 | 17 | 344 | 48 | 303 | 28 | NA | 600 | 0.2 | 22.35 | 1700000
2022-06-05 | 84770 | 84.77 | 7.35 | 7.67 | 135 | 18 | 348 | 44 | 298 | 26 | NA | 500 | 0.2 | 21.95 | 1400000
2022-06-06 | 82140 | 82.14 | 7.44 | 7.69 | 140 | 16 | 336 | 40 | 309 | 29 | NA | 600 | 0.3 | 22.25 | 1500000
2022-06-07 | 84550 | 84.55 | 7.42 | 7.71 | 145 | 19 | 332 | 44 | 299 | 26 | NA | 500 | 0.2 | 21.36 | 1300000
2022-06-08 | 81860 | 81.86 | 7.45 | 7.68 | 130 | 17 | 348 | 40 | 288 | 24 | NA | 400 | 0.2 | 21.49 | 1400000
2022-06-09 | 83240 | 83.24 | 7.38 | 7.66 | 135 | 16 | 328 | 36 | 312 | 25 | NA | 600 | 0.3 | 22.17 | 1700000
2022-06-10 | 83020 | 83.02 | 7.41 | 7.65 | 140 | 18 | 336 | 40 | 295 | 27 | NA | 500 | 0.2 | 22.61 | 1400000
2022-06-11 | 80400 | 80.4 | 7.43 | 7.67 | 135 | 19 | 340 | 44 | 305 | 28 | NA | 400 | 0.2 | 21.79 | 1300000
2022-06-12 | 76460 | 76.46 | 7.39 | 7.71 | 125 | 15 | 324 | 36 | 287 | 23 | NA | 500 | 0.3 | 22.25 | 1700000
2022-06-13 | 70330 | 70.33 | 7.44 | 7.65 | 130 | 17 | 320 | 40 | 285 | 25 | NA | 600 | 0.2 | 21.79 | 1400000
2022-06-14 | 72480 | 72.48 | 7.37 | 7.68 | 125 | 18 | 328 | 44 | 296 | 24 | NA | 400 | 0.2 | 22.65 | 1700000
2022-06-15 | 82540 | 82.54 | 7.4 | 7.72 | 140 | 16 | 336 | 40 | 298 | 27 | NA | 500 | 0.2 | 21.26 | 1300000
2022-06-16 | 85080 | 85.08 | 7.45 | 7.67 | 135 | 19 | 348 | 48 | 308 | 29 | NA | 600 | 0.2 | 23.05 | 1700000
2022-06-17 | 95900 | 95.9 | 7.43 | 7.65 | 145 | 18 | 344 | 40 | 312 | 26 | NA | 500 | 0.2 | 22.67 | 1400000
2022-06-18 | 89300 | 89.3 | 7.42 | 7.68 | 140 | 19 | 348 | 44 | 299 | 28 | NA | 400 | 0.2 | 21.39 | 1700000
2022-06-19 | 83000 | 83 | 7.39 | 7.63 | 130 | 16 | 328 | 36 | 305 | 23 | NA | 600 | 0.3 | 23.07 | 1400000
2022-06-20 | 89320 | 89.32 | 7.45 | 7.7 | 135 | 18 | 340 | 44 | 315 | 25 | NA | 500 | 0.2 | 22.03 | 1300000
2022-06-21 | 93680 | 93.68 | 7.41 | 7.66 | 145 | 17 | 348 | 40 | 307 | 27 | NA | 600 | 0.2 | 21.76 | 1700000
2022-06-22 | 89860 | 89.86 | 7.37 | 7.67 | 140 | 18 | 336 | 44 | 295 | 29 | NA | 400 | 0.2 | 22.83 | 1400000
2022-06-23 | 87740 | 87.74 | 7.35 | 7.68 | 135 | 17 | 332 | 36 | 287 | 26 | NA | 500 | 0.2 | 22.45 | 1700000
2022-06-24 | 85110 | 85.11 | 7.42 | 7.71 | 130 | 16 | 328 | 40 | 281 | 24 | NA | 600 | 0.3 | 21.79 | 1400000
2022-06-25 | 81940 | 81.94 | 7.39 | 7.65 | 125 | 18 | 324 | 44 | 293 | 28 | NA | 400 | 0.2 | 22.27 | 1300000
2022-06-26 | 90930 | 90.93 | 7.43 | 7.72 | 140 | 19 | 344 | 48 | 309 | 25 | NA | 600 | 0.2 | 22.83 | 1700000
2022-06-27 | 90450 | 90.45 | 7.38 | 7.69 | 135 | 17 | 336 | 44 | 315 | 27 | NA | 500 | 0.2 | 21.39 | 1400000
2022-06-28 | 86680 | 86.68 | 7.4 | 7.67 | 130 | 15 | 328 | 40 | 289 | 24 | NA | 600 | 0.3 | 21.73 | 1300000
2022-06-29 | 89370 | 89.37 | 7.36 | 7.68 | 140 | 18 | 332 | 44 | 295 | 26 | NA | 400 | 0.2 | 22.57 | 1400000
2022-06-30 | 96080 | 96.08 | 7.42 | 7.7 | 130 | 15 | 348 | 48 | 305 | 29 | NA | 600 | 0.3 | 22.16 | 1700000
Average | 84665 | 84.665 | 7.4047 | 7.6743 | 134.3333 | 17.1667 | 336.4 | 41.8667 | 298.6 | 26.1333 | NA | 513.3333 | 0.22667 | 22.132 | 1490000
2539.95
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 70330 | 70.33 | 7.35 | 7.58 | 125 | 15 | 320 | 36 | 281 | 23 |  | 400 | 0.2 | 21.26 | 1300000
Max | 96080 | 96.08 | 7.45 | 7.72 | 145 | 19 | 348 | 48 | 315 | 29 |  | 600 | 0.3 | 23.07 | 1700000