## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-03-01 | 133060 | 113.06 | 7.45 | 7.58 | 125 | 29 | 344 | 43 | 310 | 38 | NA | 400 | 0.3 | 24.72 | 1300000
2023-03-02 | 109950 | 109.95 | 7.39 | 7.5 | 120 | 27 | 352 | 44 | 312 | 39 | NA | 800 | 0.2 | 25.1 | 1400000
2023-03-03 | 109510 | 109.51 | 7.31 | 7.46 | 130 | 29 | 356 | 48 | 315 | 43 | NA | 500 | 0.3 | 24.5 | 1700000
2023-03-04 | 110980 | 110.98 | 7.3 | 7.44 | 145 | 28 | 340 | 44 | 307 | 40 | NA | 700 | 0.2 | 24.91 | 1300000
2023-03-05 | 110420 | 110.42 | 7.24 | 7.42 | 120 | 29 | 328 | 43 | 311 | 38 | NA | 600 | 0.3 | 25.31 | 1400000
2023-03-06 | 113150 | 113.15 | 7.32 | 7.51 | 125 | 28 | 336 | 45 | 304 | 39 | NA | 400 | 0.2 | 24.17 | 1700000
2023-03-07 | 114990 | 114.99 | 7.25 | 7.42 | 135 | 29 | 320 | 42 | 301 | 37 | NA | 800 | 0.2 | 25.23 | 1400000
2023-03-08 | 140250 | 140.25 | 7.37 | 7.52 | 140 | 30 | 308 | 44 | 297 | 38 | NA | 600 | 0.3 | 24.57 | 1200000
2023-03-09 | 139390 | 139.39 | 7.28 | 7.58 | 130 | 28 | 316 | 40 | 299 | 36 | NA | 500 | 0.3 | 24.2 | 1700000
2023-03-10 | 122440 | 122.44 | 7.31 | 7.5 | 125 | 30 | 312 | 42 | 287 | 35 | NA | 700 | 0.2 | 25.03 | 1400000
2023-03-11 | 116020 | 116.02 | 7.3 | 7.48 | 130 | 29 | 318 | 40 | 301 | 34 | NA | 400 | 0.2 | 24.61 | 1300000
2023-03-12 | 11413 | 114.13 | 7.24 | 7.55 | 120 | 30 | 336 | 44 | 298 | 38 | NA | 600 | 0.3 | 24.64 | 1400000
2023-03-13 | 116720 | 116.72 | 7.33 | 7.47 | 125 | 29 | 330 | 42 | 291 | 36 | NA | 800 | 0.3 | 25.12 | 1700000
2023-03-14 | 116690 | 116.69 | 7.44 | 7.53 | 130 | 27 | 324 | 44 | 307 | 36 | NA | 600 | 0.2 | 25.7 | 1300000
2023-03-15 | 114390 | 114.39 | 7.4 | 7.56 | 145 | 28 | 316 | 44 | 288 | 39 | NA | 400 | 0.2 | 25.1 | 1700000
2023-03-16 | 114390 | 114.39 | 7.3 | 7.5 | 120 | 27 | 320 | 45 | 293 | 40 | NA | 700 | 0.3 | 25.2 | 1400000
2023-03-17 | 94630 | 94.63 | 7.18 | 7.58 | 125 | 28 | 328 | 42 | 301 | 37 | NA | 500 | 0.3 | 24.51 | 1200000 | Due to state level strike organised by UPPCL staff, water supply to various areas of Prayagraj was reduced because of several power cuts. Hence, raw sewage generated was less.
2023-03-18 | 57100 | 57.1 | 7.14 | 7.43 | 145 | 27 | 356 | 43 | 289 | 36 | NA | 800 | 0.2 | 24.16 | 1700000
2023-03-19 | 74670 | 74.67 | 7.25 | 7.62 | 150 | 29 | 350 | 42 | 293 | 35 | NA | 600 | 0.3 | 25.11 | 1300000
2023-03-20 | 120740 | 120.74 | 7.18 | 7.6 | 130 | 30 | 342 | 44 | 284 | 38 | NA | 400 | 0.2 | 24.5 | 1400000
2023-03-21 | 119170 | 119.17 | 7.37 | 7.63 | 120 | 28 | 334 | 45 | 281 | 40 | NA | 700 | 0.3 | 24.73 | 1700000
2023-03-22 | 123910 | 123.91 | 7.3 | 7.59 | 125 | 27 | 326 | 44 | 298 | 39 | NA | 500 | 0.2 | 25.13 | 1200000
2023-03-23 | 117640 | 115.64 | 7.42 | 7.61 | 130 | 28 | 322 | 41 | 287 | 36 | NA | 800 | 0.2 | 24.33 | 1400000
2023-03-24 | 93250 | 93.25 | 7.44 | 7.59 | 140 | 26 | 342 | 40 | 300 | 35 | NA | 600 | 0.3 | 25.06 | 1700000
2023-03-25 | 97220 | 97.22 | 7.11 | 6.92 | 125 | 25 | 314 | 39 | 291 | 34 | NA | 400 | 0.3 | 25.21 | 1200000
2023-03-26 | 116720 | 116.72 | 7.49 | 7.58 | 140 | 30 | 345 | 45 | 288 | 41 | NA | 500 | 0.2 | 24.3 | 1300000
2023-03-27 | 121890 | 121.89 | 7.3 | 7.56 | 150 | 28 | 354 | 42 | 302 | 38 | NA | 700 | 0.2 | 24.86 | 1400000
2023-03-28 | 122360 | 122.36 | 7.33 | 7.59 | 130 | 27 | 338 | 44 | 299 | 39 | NA | 600 | 0.3 | 25.18 | 1700000
2023-03-29 | 115150 | 115.15 | 7.48 | 7.51 | 125 | 28 | 342 | 47 | 295 | 43 | NA | 500 | 0.3 | 24.27 | 1200000
2023-03-30 | 113600 | 113.6 | 7.37 | 7.54 | 135 | 27 | 346 | 44 | 302 | 40 | NA | 800 | 0.2 | 25.06 | 1400000
2023-03-31 | 117620 | 117.62 | 7.33 | 7.58 | 145 | 28 | 352 | 42 | 305 | 38 | NA | 400 | 0.3 | 25.1 | 1700000
Average | 109659.129 | 112.2629 | 7.32 | 7.5145 | 131.6129 | 28.1613 | 333.7742 | 43.1613 | 297.9355 | 37.9032 | NA | 590.3226 | 0.25161 | 24.8265 | 1445161.2903
3480.15
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11413 | 57.1 | 7.11 | 6.92 | 120 | 25 | 308 | 39 | 281 | 34 |  | 400 | 0.2 | 24.16 | 1200000
Max | 140250 | 140.25 | 7.49 | 7.63 | 150 | 30 | 356 | 48 | 315 | 43 |  | 800 | 0.3 | 25.7 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-03-01 | 73480 | 73.48 | 7.28 | 7.58 | 130 | 17 | 328 | 40 | 291 | 27 | NA | 500 | 0.2 | 23.15 | 1700000
2023-03-02 | 71870 | 71.87 | 7.26 | 7.6 | 135 | 18 | 324 | 44 | 289 | 28 | NA | 600 | 0.3 | 25.04 | 1400000
2023-03-03 | 72680 | 72.68 | 7.3 | 7.62 | 125 | 16 | 332 | 40 | 305 | 26 | NA | 700 | 0.3 | 22.39 | 1700000
2023-03-04 | 69690 | 69.69 | 7.28 | 7.61 | 130 | 18 | 316 | 44 | 285 | 25 | NA | 600 | 0.2 | 23.79 | 1300000
2023-03-05 | 74150 | 74.15 | 7.31 | 7.66 | 128 | 18 | 324 | 40 | 297 | 27 | NA | 700 | 0.3 | 23.75 | 1400000
2023-03-06 | 72080 | 72.08 | 7.29 | 7.67 | 135 | 17 | 320 | 44 | 287 | 26 | NA | 500 | 0.2 | 24.13 | 1700000
2023-03-07 | 71940 | 71.94 | 7.33 | 7.68 | 130 | 18 | 328 | 40 | 307 | 25 | NA | 400 | 0.2 | 23.61 | 1400000
2023-03-08 | 76720 | 76.72 | 7.31 | 7.67 | 125 | 16 | 312 | 44 | 279 | 27 | NA | 600 | 0.3 | 25.53 | 1400000
2023-03-09 | 76220 | 76.22 | 7.26 | 7.6 | 130 | 17 | 324 | 40 | 287 | 26 | NA | 400 | 0.3 | 24.82 | 1300000
2023-03-10 | 73810 | 73.81 | 7.31 | 7.53 | 135 | 16 | 320 | 36 | 286 | 27 | NA | 700 | 0.3 | 26.78 | 1400000
2023-03-11 | 70110 | 70.1 | 7.28 | 7.64 | 140 | 17 | 328 | 44 | 295 | 25 | NA | 600 | 0.2 | 23.63 | 1700000
2023-03-12 | 72400 | 72.4 | 7.32 | 7.66 | 125 | 16 | 316 | 36 | 307 | 26 | NA | 500 | 0.3 | 24.69 | 1400000
2023-03-13 | 73700 | 73.7 | 7.27 | 7.65 | 140 | 18 | 324 | 40 | 289 | 25 | NA | 700 | 0.2 | 23.78 | 1700000
2023-03-14 | 71700 | 71.7 | 7.29 | 7.66 | 145 | 19 | 336 | 44 | 278 | 27 | NA | 600 | 0.3 | 25.43 | 1300000
2023-03-15 | 75450 | 75.45 | 7.26 | 7.61 | 140 | 18 | 328 | 40 | 292 | 26 | NA | 500 | 0.2 | 23.5 | 1400000
2023-03-16 | 73980 | 73.98 | 7.28 | 7.64 | 135 | 17 | 312 | 44 | 285 | 27 | NA | 400 | 0.3 | 23.82 | 1300000
2023-03-17 | 69250 | 69.25 | 7.31 | 7.63 | 125 | 16 | 324 | 40 | 297 | 26 | NA | 600 | 0.2 | 24.33 | 1700000 | Due to state level strike organised by UPPCL staff, water supply to various areas of Prayagraj was reduced because of several power cuts. Hence, raw sewage generated was less.
2023-03-18 | 59740 | 59.74 | 7.24 | 7.54 | 130 | 17 | 312 | 44 | 288 | 27 | NA | 500 | 0.3 | 25.65 | 1400000
2023-03-19 | 62830 | 62.83 | 7.32 | 7.67 | 125 | 16 | 336 | 40 | 278 | 25 | NA | 400 | 0.2 | 23.35 | 1300000
2023-03-20 | 78900 | 78.9 | 7.44 | 7.64 | 130 | 17 | 308 | 44 | 280 | 26 | NA | 700 | 0.2 | 24.58 | 1700000
2023-03-21 | 70560 | 70.56 | 7.33 | 7.6 | 140 | 18 | 320 | 44 | 285 | 26 | NA | 600 | 0.3 | 25.21 | 1400000
2023-03-22 | 72690 | 72.69 | 7.29 | 7.65 | 135 | 17 | 312 | 40 | 278 | 27 | NA | 500 | 0.2 | 23.78 | 1700000
2023-03-23 | 69010 | 69.01 | 7.34 | 7.61 | 140 | 18 | 324 | 44 | 291 | 26 | NA | 400 | 0.3 | 23.63 | 1300000
2023-03-24 | 70340 | 70.34 | 7.32 | 7.63 | 125 | 17 | 332 | 48 | 286 | 27 | NA | 700 | 0.2 | 23.34 | 1400000
2023-03-25 | 74640 | 74.64 | 7.33 | 7.59 | 145 | 18 | 324 | 40 | 285 | 25 | NA | 600 | 0.3 | 24.51 | 1700000
2023-03-26 | 74130 | 74.13 | 7.23 | 7.54 | 140 | 16 | 316 | 44 | 296 | 28 | NA | 500 | 0.3 | 23.74 | 1300000
2023-03-27 | 76570 | 76.57 | 7.31 | 7.57 | 135 | 17 | 328 | 48 | 305 | 29 | NA | 700 | 0.2 | 24.59 | 1400000
2023-03-28 | 69280 | 69.28 | 7.29 | 7.58 | 125 | 18 | 324 | 44 | 288 | 27 | NA | 600 | 0.3 | 22.85 | 1300000
2023-03-29 | 72830 | 72.83 | 7.26 | 7.57 | 140 | 16 | 332 | 48 | 293 | 26 | NA | 400 | 0.2 | 23.76 | 1700000
2023-03-30 | 70610 | 70.61 | 7.25 | 7.56 | 135 | 19 | 336 | 44 | 290 | 25 | NA | 500 | 0.3 | 23.61 | 1400000
2023-03-31 | 71690 | 71.63 | 7.25 | 7.65 | 130 | 17 | 328 | 40 | 295 | 27 | NA | 400 | 0.2 | 24.37 | 1300000
Average | 72033.871 | 72.0316 | 7.2948 | 7.6165 | 133.1613 | 17.1935 | 323.4839 | 42.3226 | 290.129 | 26.3548 | NA | 551.6129 | 0.25161 | 24.1658 | 1467741.9355
2232.98
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 59740 | 59.74 | 7.23 | 7.53 | 125 | 16 | 308 | 36 | 278 | 25 |  | 400 | 0.2 | 22.39 | 1300000
Max | 78900 | 78.9 | 7.44 | 7.68 | 145 | 19 | 336 | 48 | 307 | 29 |  | 700 | 0.3 | 26.78 | 1700000