## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 |  | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-03-01 | 112430 | 112.43 | 7.31 | 7.36 | 143 | 18 | 344 | 40 | 307 | 35 | NA | 400 | 0.3 | 25.5 | 1100000
2022-03-02 | 108180 | 108.18 | 7.33 | 7.41 | 146 | 19 | 356 | 36 | 309 | 32 | NA | 600 | 0.2 | 25.8 | 1200000
2022-03-03 | 112180 | 112.18 | 7.29 | 7.35 | 139 | 21 | 348 | 40 | 315 | 30 | NA | 500 | 0.3 | 25.9 | 1400000
2022-03-04 | 113650 | 113.65 | 7.33 | 7.36 | 133 | 23 | 336 | 44 | 311 | 32 | NA | 700 | 0.2 | 25.6 | 1300000
2022-03-05 | 111570 | 111.57 | 7.31 | 7.38 | 139 | 20 | 348 | 40 | 308 | 35 | NA | 200 | 0.3 | 25.8 | 1700000
2022-03-06 | 110440 | 110.44 | 7.33 | 7.41 | 146 | 22 | 352 | 44 | 312 | 33 | NA | 400 | 0.2 | 25.7 | 1200000
2022-03-07 | 111860 | 111.86 | 7.35 | 7.39 | 135 | 23 | 344 | 48 | 307 | 34 | NA | 500 | 0.3 | 25.03 | 1400000
2022-03-08 | 111900 | 111.9 | 7.29 | 7.34 | 140 | 21 | 352 | 40 | 313 | 36 | NA | 600 | 0.2 | 25.4 | 1700000
2022-03-09 | 103550 | 103.55 | 7.36 | 7.39 | 146 | 22 | 344 | 44 | 306 | 32 | NA | 400 | 0.3 | 25.7 | 1300000
2022-03-10 | 108710 | 108.71 | 7.28 | 7.34 | 149 | 24 | 360 | 48 | 309 | 35 | NA | 500 | 0.2 | 25.6 | 1400000 | For 10.03.2022 & 11.03.2022, sludge consistency was determined from slduge of sludge drying beds hence it cannot be deemed as accurate.
2022-03-11 | 109300 | 109.3 | 7.33 | 7.39 | 146 | 20 | 348 | 40 | 312 | 33 | NA | 600 | 0.3 | 22.8 | 1600000
2022-03-12 | 107840 | 107.84 | 7.24 | 7.48 | 143 | 21 | 356 | 44 | 320 | 31 | NA | 400 | 0.2 | 23.5 | 1200000
2022-03-13 | 103920 | 103.92 | 7.27 | 7.36 | 136 | 20 | 336 | 40 | 308 | 34 | NA | 600 | 0.2 | 24.7 | 1300000
2022-03-14 | 109890 | 109.89 | 7.32 | 7.38 | 146 | 24 | 352 | 48 | 306 | 32 | NA | 700 | 0.3 | 25.2 | 1700000
2022-03-15 | 114890 | 114.89 | 7.29 | 7.35 | 139 | 20 | 344 | 44 | 302 | 34 | NA | 500 | 0.2 | 25.6 | 1400000
2022-03-16 | 99020 | 99.02 | 7.28 | 7.37 | 143 | 19 | 352 | 40 | 309 | 32 | NA | 600 | 0.3 | 25.4 | 1700000
2022-03-17 | 108810 | 108.81 | 7.31 | 7.36 | 146 | 21 | 356 | 44 | 315 | 34 | NA | 400 | 0.2 | 25.6 | 1600000
2022-03-18 | 136420 | 136.42 | 6.88 | 7.03 | 156 | 25 | 380 | 48 | 312 | 32 | NA | 700 | 0.3 | 25.8 | 1400000
2022-03-19 | 135820 | 135.82 | 6.98 | 7.09 | 153 | 26 | 368 | 48 | 308 | 33 | NA | 600 | 0.2 | 25.9 | 1200000 | For 19.03.2022 & 20.03.2022, sludge consistency was determined from slduge of sludge drying beds hence it cannot be deemed as accurate.
2022-03-20 | 121060 | 121.06 | 7.02 | 7.23 | 149 | 24 | 356 | 40 | 313 | 36 | NA | 400 | 0.3 | 25.6 | 1300000
2022-03-21 | 109820 | 109.82 | 7.19 | 7.28 | 146 | 22 | 352 | 44 | 309 | 33 | NA | 500 | 0.2 | 25.4 | 1700000
2022-03-22 | 107030 | 107.03 | 7.22 | 7.32 | 143 | 20 | 344 | 40 | 307 | 31 | NA | 700 | 0.3 | 26 | 1100000
2022-03-23 | 100170 | 100.17 | 7.28 | 7.36 | 149 | 21 | 340 | 44 | 311 | 33 | NA | 500 | 0.2 | 25.8 | 1200000
2022-03-24 | 108170 | 108.17 | 7.33 | 7.39 | 153 | 20 | 348 | 40 | 313 | 31 | NA | 700 | 0.3 | 25.4 | 1400000
2022-03-25 | 103010 | 103.01 | 7.33 | 7.34 | 156 | 22 | 352 | 44 | 308 | 33 | NA | 600 | 0.2 | 25.2 | 1300000
2022-03-26 | 102760 | 102.76 | 7.32 | 7.39 | 146 | 20 | 344 | 40 | 306 | 31 | NA | 700 | 0.2 | 25.6 | 1400000
2022-03-27 | 104580 | 104.58 | 7.36 | 7.41 | 153 | 24 | 360 | 48 | 310 | 35 | NA | 500 | 0.3 | 25.9 | 1700000
2022-03-28 | 104180 | 104.18 | 7.38 | 7.39 | 149 | 20 | 352 | 40 | 305 | 32 | NA | 700 | 0.2 | 25.9 | 1400000
2022-03-29 | 49570 | 49.57 | 7.33 | 7.36 | 143 | 18 | 340 | 36 | 308 | 30 | NA | 600 | 0.3 | 26.2 | 1300000 | Gaughat MPS & Chacharnalla SPS were stopped and sewage was bypassed at 11:15 AM on 29.03.2022 due to maintenance work of new line fom Gaughat MPS to Naini-I STP. Subsequently, Naini-I STP was also stopped.
2022-03-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 25.5 | 1700000
2022-03-31 | 42510 | 42.51 | 7.39 | 7.44 | 153 | 21 | 356 | 44 | 303 | 33 | NA | 500 | 0.2 | 25.46 | 1200000 | Gaughat MPS & Chacharnalla SPS were started at 3:00 PM. Only new line was started since maintenance work in new line fom Gaughat MPS to Naini-I STP was in progress. Subsequently, Naini-I STP was also started.
Average | 102685.1613 | 102.6852 | 7.2743 | 7.3483 | 145.4667 | 21.3667 | 350.6667 | 42.6667 | 309.4 | 32.9 | NA | 543.3333 | 0.24667 | 25.4352 | 1403225.8065
3183.24
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 42510 | 42.51 | 6.88 | 7.03 | 133 | 18 | 336 | 36 | 302 | 30 |  | 200 | 0.2 | 22.8 | 1100000
Max | 136420 | 136.42 | 7.39 | 7.48 | 156 | 26 | 380 | 48 | 320 | 36 |  | 700 | 0.3 | 26.2 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-03-01 | 80350 | 80.35 | 7.42 | 7.73 | 140 | 15 | 336 | 40 | 275 | 24 | NA | 600 | 0.2 | 22.21 | 1700000 | Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-03-02 | 77580 | 77.58 | 7.38 | 7.69 | 130 | 16 | 348 | 48 | 280 | 27 | NA | 400 | 0.2 | 22.01 | 1400000
2022-03-03 | 79380 | 79.38 | 7.45 | 7.65 | 135 | 18 | 304 | 44 | 292 | 25 | NA | 700 | 0.2 | 21.33 | 1300000
2022-03-04 | 76920 | 76.92 | 7.41 | 7.73 | 145 | 16 | 324 | 40 | 289 | 23 | NA | 500 | 0.2 | 22.25 | 1700000
2022-03-05 | 78130 | 78.13 | 7.42 | 7.75 | 130 | 17 | 328 | 48 | 295 | 26 | NA | 400 | 0.2 | 23.25 | 1400000
2022-03-06 | 77420 | 77.42 | 7.32 | 7.68 | 135 | 15 | 312 | 36 | 279 | 29 | NA | 600 | 0.2 | 21.37 | 1400000
2022-03-07 | 76580 | 76.58 | 7.39 | 7.71 | 125 | 14 | 340 | 44 | 283 | 28 | NA | 500 | 0.3 | 22.95 | 1700000
2022-03-08 | 75770 | 75.77 | 7.43 | 7.72 | 130 | 17 | 316 | 40 | 297 | 27 | NA | 400 | 0.2 | 22.77 | 1300000
2022-03-09 | 78180 | 78.18 | 7.4 | 7.69 | 140 | 18 | 344 | 44 | 285 | 25 | NA | 600 | 0.2 | 21.38 | 1400000
2022-03-10 | 75840 | 75.84 | 7.38 | 7.74 | 145 | 16 | 328 | 40 | 305 | 23 | NA | 500 | 0.2 | 22.93 | 1700000
2022-03-11 | 79350 | 79.35 | 7.42 | 7.75 | 135 | 15 | 312 | 48 | 299 | 28 | NA | 400 | 0.2 | 21.95 | 1700000
2022-03-12 | 76810 | 76.81 | 7.34 | 7.73 | 130 | 17 | 316 | 44 | 278 | 26 | NA | 400 | 0.2 | 22.68 | 1400000
2022-03-13 | 80310 | 80.31 | 7.39 | 7.67 | 140 | 16 | 344 | 44 | 291 | 24 | NA | 600 | 0.2 | 21.33 | 1700000
2022-03-14 | 78900 | 78.9 | 7.41 | 7.72 | 125 | 18 | 336 | 40 | 303 | 25 | NA | 500 | 0.3 | 22.85 | 1400000
2022-03-15 | 79110 | 79.11 | 7.37 | 7.71 | 135 | 17 | 328 | 44 | 289 | 29 | NA | 700 | 0.2 | 21.39 | 1300000
2022-03-16 | 78020 | 78.02 | 7.33 | 7.69 | 145 | 16 | 340 | 48 | 297 | 27 | NA | 600 | 0.2 | 23.15 | 1700000
2022-03-17 | 71580 | 71.58 | 7.4 | 7.73 | 130 | 19 | 316 | 48 | 279 | 28 | NA | 400 | 0.2 | 22.88 | 1300000
2022-03-18 | 86330 | 86.33 | 7.32 | 7.65 | 125 | 18 | 336 | 40 | 288 | 24 | NA | 500 | 0.3 | 21.85 | 1400000
2022-03-19 | 81550 | 81.55 | 7.37 | 7.72 | 140 | 17 | 344 | 44 | 295 | 25 | NA | 600 | 0.2 | 22.57 | 1700000
2022-03-20 | 74140 | 74.14 | 7.42 | 7.75 | 135 | 16 | 328 | 48 | 298 | 26 | NA | 400 | 0.2 | 22.69 | 1700000
2022-03-21 | 76510 | 76.51 | 7.39 | 7.71 | 125 | 17 | 348 | 40 | 306 | 29 | NA | 500 | 0.2 | 23.03 | 1400000
2022-03-22 | 71670 | 71.67 | 7.43 | 7.75 | 130 | 19 | 340 | 44 | 293 | 27 | NA | 600 | 0.2 | 22.65 | 1300000
2022-03-23 | 76580 | 76.58 | 7.38 | 7.73 | 140 | 18 | 328 | 48 | 279 | 25 | NA | 400 | 0.2 | 21.39 | 1700000
2022-03-24 | 72580 | 72.58 | 7.41 | 7.69 | 135 | 18 | 344 | 36 | 296 | 28 | NA | 500 | 0.3 | 22.75 | 1400000
2022-03-25 | 73640 | 73.64 | 7.42 | 7.74 | 125 | 16 | 336 | 40 | 305 | 24 | NA | 400 | 0.2 | 23.57 | 1700000
2022-03-26 | 28280 | 28.28 | 7.39 | 7.69 | 130 | 17 | 312 | 44 | 275 | 27 | NA | 600 | 0.2 | 22.68 | 1700000 | 1) On 26.03.2022, Mumfordganj SPS was shutdown at 8:00 AM for diverting the rising main from Mumfordganj SPS to Rajapur STP due to ongoing construction of Expressway. 2) Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-03-27 | 8510 | 8.51 | 7.37 | 7.74 | 140 | 15 | 324 | 48 | 289 | 25 | NA | 400 | 0.2 | 23.63 | 1400000
2022-03-28 | 12620 | 12.62 | 7.37 | 7.72 | 135 | 16 | 320 | 44 | 301 | 23 | NA | 500 | 0.2 | 22.45 | 1700000
2022-03-29 | 9230 | 9.23 | 7.4 | 7.68 | 125 | 14 | 332 | 40 | 285 | 26 | NA | 600 | 0.2 | 23.15 | 1400000
2022-03-30 | 16910 | 16.91 | 7.42 | 7.73 | 135 | 13 | 328 | 44 | 294 | 27 | NA | 400 | 0.2 | 21.25 | 1300000
2022-03-31 | 20430 | 20.43 | 7.39 | 7.68 | 130 | 16 | 316 | 36 | 309 | 25 | NA | 400 | 0.2 | 21.86 | 1700000
Average | 65458.3871 | 65.4584 | 7.3916 | 7.7119 | 133.7097 | 16.4516 | 329.2903 | 43.0968 | 291.2581 | 25.9677 | NA | 503.2258 | 0.2129 | 22.3935 | 1516129.0323
2029.21
Source: |  | Logbook of Labarotory at Sewage Treament Plant | [14 empty] | 1 Apr, 9:40 AM
Min | 8510 | 8.51 | 7.32 | 7.65 | 125 | 13 | 304 | 36 | 275 | 23 |  | 400 | 0.2 | 21.25 | 1300000
Max | 86330 | 86.33 | 7.45 | 7.75 | 145 | 19 | 348 | 48 | 309 | 29 |  | 700 | 0.3 | 23.63 | 1700000