## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-05-01 | 125070 | 125.07 | 7.28 | 7.36 | 133 | 20 | 332 | 40 | 298 | 35 | NA | 500 | 0.3 | 26.1 | 1400000
2022-05-02 | 125880 | 125.88 | 7.33 | 7.44 | 129 | 22 | 340 | 44 | 305 | 31 | NA | 600 | 0.3 | 25.7 | 1700000
2022-05-03 | 119030 | 119.03 | 7.35 | 7.39 | 136 | 24 | 348 | 48 | 307 | 36 | NA | 700 | 0.2 | 25.8 | 1300000
2022-05-04 | 121030 | 121.03 | 7.28 | 7.37 | 129 | 20 | 328 | 40 | 309 | 34 | NA | 400 | 0.2 | 25.6 | 1200000 | Sample of Sludge was taken from Sludge dryng beds hence sludge consistency cannot be deemed as accurate.
2022-05-05 | 111210 | 111.21 | 7.35 | 7.39 | 133 | 22 | 336 | 44 | 302 | 32 | NA | 500 | 0.3 | 25.3 | 1400000
2022-05-06 | 113130 | 113.13 | 7.28 | 7.34 | 139 | 24 | 340 | 48 | 306 | 35 | NA | 700 | 0.3 | 25.3 | 1300000
2022-05-07 | 115360 | 115.36 | 7.33 | 7.36 | 136 | 19 | 356 | 40 | 302 | 33 | NA | 600 | 0.2 | 25.2 | 1200000
2022-05-08 | 118860 | 118.86 | 7.28 | 7.35 | 129 | 18 | 328 | 36 | 298 | 32 | NA | 500 | 0.3 | 25.7 | 1700000
2022-05-09 | 118810 | 118.81 | 7.33 | 7.38 | 133 | 20 | 336 | 44 | 305 | 33 | NA | 400 | 0.3 | 25.3 | 1300000
2022-05-10 | 115360 | 115.36 | 7.39 | 7.44 | 136 | 22 | 344 | 40 | 304 | 32 | NA | 700 | 0.2 | 25.1 | 1400000
2022-05-11 | 116650 | 116.65 | 7.44 | 7.46 | 139 | 24 | 352 | 48 | 309 | 30 | NA | 600 | 0.2 | 25.9 | 1300000
2022-05-12 | 118480 | 118.48 | 7.33 | 7.41 | 136 | 19 | 340 | 40 | 306 | 32 | NA | 500 | 0.3 | 24.7 | 1200000
2022-05-13 | 118640 | 118.64 | 7.28 | 7.36 | 143 | 23 | 348 | 44 | 305 | 35 | NA | 600 | 0.3 | 24.9 | 1700000
2022-05-14 | 117800 | 117.8 | 7.33 | 7.76 | 129 | 20 | 336 | 40 | 307 | 33 | NA | 400 | 0.3 | 25.1 | 1400000
2022-05-15 | 118080 | 118.08 | 7.32 | 7.38 | 133 | 18 | 328 | 36 | 303 | 29 | NA | 700 | 0.2 | 25.3 | 1300000
2022-05-16 | 117560 | 117.56 | 7.28 | 7.36 | 139 | 23 | 344 | 44 | 305 | 32 | NA | 500 | 0.3 | 25.7 | 1200000
2022-05-17 | 113620 | 113.62 | 7.31 | 7.35 | 129 | 21 | 352 | 40 | 302 | 31 | NA | 600 | 0.2 | 25.3 | 1700000
2022-05-18 | 113830 | 113.83 | 7.33 | 7.39 | 136 | 24 | 356 | 48 | 298 | 30 | NA | 400 | 0.3 | 25.1 | 1400000
2022-05-19 | 112660 | 112.66 | 7.28 | 7.36 | 129 | 18 | 328 | 36 | 294 | 29 | NA | 700 | 0.2 | 25.6 | 1300000
2022-05-20 | 115820 | 115.82 | 7.33 | 7.44 | 133 | 20 | 336 | 40 | 303 | 32 | NA | 400 | 0.3 | 25.3 | 1200000
2022-05-21 | 98870 | 98.87 | 7.28 | 7.36 | 136 | 22 | 340 | 44 | 298 | 32 | NA | 600 | 0.3 | 25 | 1700000
2022-05-22 | 104320 | 104.32 | 7.35 | 7.41 | 133 | 18 | 344 | 36 | 309 | 33 | NA | 500 | 0.2 | 24.4 | 1400000
2022-05-23 | 110100 | 110.1 | 7.28 | 7.33 | 129 | 21 | 348 | 40 | 296 | 35 | NA | 700 | 0.2 | 25.3 | 1300000
2022-05-24 | 118390 | 118.39 | 7.32 | 7.36 | 136 | 19 | 328 | 36 | 299 | 33 | NA | 400 | 0.3 | 25.4 | 1700000
2022-05-25 | 121170 | 121.17 | 7.24 | 7.34 | 139 | 17 | 336 | 44 | 305 | 31 | NA | 600 | 0.3 | 25.2 | 1200000
2022-05-26 | 121380 | 121.38 | 7.31 | 7.39 | 133 | 21 | 328 | 48 | 303 | 33 | NA | 700 | 0.2 | 25.4 | 1300000
2022-05-27 | 117510 | 117.51 | 7.33 | 7.38 | 139 | 20 | 344 | 40 | 308 | 34 | NA | 500 | 0.2 | 24.5 | 1400000
2022-05-28 | 112640 | 112.64 | 7.28 | 7.34 | 129 | 18 | 336 | 44 | 303 | 32 | NA | 600 | 0.3 | 25.3 | 1300000
2022-05-29 | 121480 | 121.48 | 7.36 | 7.38 | 136 | 21 | 340 | 40 | 308 | 35 | NA | 700 | 0.2 | 25.6 | 1700000
2022-05-30 | 115400 | 115.4 | 7.33 | 7.36 | 133 | 19 | 328 | 44 | 304 | 32 | NA | 500 | 0.2 | 25.7 | 1300000
2022-05-31 | 111460 | 111.46 | 7.31 | 7.33 | 139 | 18 | 344 | 40 | 312 | 30 | NA | 400 | 0.2 | 25.8 | 1700000
Average | 116116.129 | 116.1161 | 7.3168 | 7.3894 | 134.2258 | 20.4839 | 339.4839 | 41.8065 | 303.6452 | 32.4516 | NA | 554.8387 | 0.25161 | 25.3419 | 1406451.6129
| 3599600 | 3599.6
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 98870 | 98.87 | 7.24 | 7.33 | 129 | 17 | 328 | 36 | 294 | 29 |  | 400 | 0.2 | 24.4 | 1200000
Max | 125880 | 125.88 | 7.44 | 7.76 | 143 | 24 | 356 | 48 | 312 | 36 |  | 700 | 0.3 | 26.1 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-05-01 | 17440 | 17.44 | 7.43 | 7.65 | 120 | 12 | 316 | 36 | 279 | 24 | NA | 500 | 0.2 | 22.57 | 1300000 | 1) Mumfordganj SPS is shutdown for diverting the rising main from Mumfordganj SPS to Rajapur STP due to ongoing construction of Expressway. 2) Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-05-02 | 20990 | 20.99 | 7.39 | 7.69 | 125 | 13 | 320 | 40 | 283 | 26 | NA | 400 | 0.2 | 22.82 | 1400000
2022-05-03 | 27500 | 27.5 | 7.45 | 7.71 | 120 | 13 | 316 | 36 | 276 | 23 | NA | 500 | 0.3 | 21.99 | 1400000
2022-05-04 | 19110 | 19.11 | 7.37 | 7.67 | 120 | 12 | 324 | 36 | 288 | 25 | NA | 400 | 0.2 | 22.73 | 1200000
2022-05-05 | 19580 | 19.58 | 7.41 | 7.73 | 125 | 12 | 320 | 40 | 275 | 27 | NA | 400 | 0.2 | 23.05 | 1300000
2022-05-06 | 21360 | 21.36 | 7.35 | 7.72 | 130 | 14 | 312 | 32 | 261 | 22 | NA | 500 | 0.2 | 23.17 | 1300000
2022-05-07 | 19710 | 19.71 | 7.38 | 7.69 | 120 | 13 | 316 | 36 | 273 | 23 | NA | 500 | 0.2 | 22.98 | 1400000
2022-05-08 | 18110 | 18.11 | 7.43 | 7.67 | 120 | 12 | 312 | 32 | 262 | 21 | NA | 400 | 0.3 | 23.09 | 1300000
2022-05-09 | 30690 | 30.69 | 7.45 | 7.71 | 125 | 14 | 324 | 36 | 278 | 24 | NA | 600 | 0.2 | 22.79 | 1400000 | 1) On 09.05.2022, Mumfordganj SPS was started at 08:05 PM after completion of works. 2) Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-05-10 | 75250 | 75.25 | 7.36 | 7.68 | 135 | 15 | 344 | 44 | 291 | 28 | NA | 600 | 0.2 | 22.32 | 1700000 | Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-05-11 | 85290 | 85.29 | 7.39 | 7.73 | 140 | 18 | 348 | 48 | 315 | 29 | NA | 500 | 0.2 | 22.34 | 1700000
2022-05-12 | 82840 | 82.84 | 7.35 | 7.67 | 135 | 17 | 340 | 44 | 309 | 27 | NA | 600 | 0.3 | 23.17 | 1400000
2022-05-13 | 84890 | 84.89 | 7.42 | 7.71 | 140 | 18 | 344 | 48 | 312 | 28 | NA | 600 | 0.2 | 22.73 | 1700000
2022-05-14 | 78200 | 78.2 | 7.37 | 7.69 | 130 | 17 | 336 | 44 | 298 | 26 | NA | 400 | 0.2 | 23.05 | 1400000
2022-05-15 | 77680 | 77.68 | 7.43 | 7.72 | 125 | 16 | 340 | 40 | 311 | 25 | NA | 500 | 0.2 | 22.12 | 1700000
2022-05-16 | 85640 | 85.64 | 7.36 | 7.66 | 140 | 17 | 332 | 40 | 305 | 26 | NA | 600 | 0.2 | 21.21 | 1700000
2022-05-17 | 81130 | 81.13 | 7.45 | 7.71 | 135 | 15 | 328 | 36 | 293 | 28 | NA | 500 | 0.3 | 22.37 | 1400000
2022-05-18 | 81710 | 81.71 | 7.4 | 7.67 | 140 | 18 | 336 | 44 | 310 | 29 | NA | 600 | 0.2 | 21.85 | 1300000
2022-05-19 | 79020 | 79.02 | 7.41 | 7.72 | 130 | 16 | 332 | 40 | 298 | 27 | NA | 400 | 0.2 | 21.67 | 1700000
2022-05-20 | 82950 | 82.95 | 7.38 | 7.7 | 140 | 19 | 344 | 44 | 315 | 29 | NA | 500 | 0.2 | 21.35 | 1700000
2022-05-21 | 79560 | 79.56 | 7.35 | 7.69 | 135 | 16 | 328 | 36 | 291 | 25 | NA | 400 | 0.2 | 22.25 | 1400000
2022-05-22 | 77940 | 77.94 | 7.42 | 7.73 | 130 | 17 | 324 | 40 | 283 | 23 | NA | 600 | 0.3 | 22.71 | 1300000
2022-05-23 | 70050 | 70.05 | 7.36 | 7.65 | 125 | 18 | 320 | 40 | 279 | 24 | NA | 500 | 0.2 | 21.87 | 1400000
2022-05-24 | 82220 | 82.22 | 7.43 | 7.68 | 140 | 19 | 344 | 44 | 314 | 28 | NA | 400 | 0.2 | 22.07 | 1300000
2022-05-25 | 84140 | 84.14 | 7.4 | 7.66 | 135 | 18 | 340 | 40 | 297 | 26 | NA | 600 | 0.3 | 22.18 | 1700000
2022-05-26 | 76230 | 76.23 | 7.44 | 7.71 | 130 | 15 | 336 | 36 | 282 | 27 | NA | 400 | 0.2 | 21.75 | 1400000
2022-05-27 | 85910 | 85.91 | 7.35 | 7.68 | 125 | 19 | 348 | 44 | 305 | 29 | NA | 500 | 0.2 | 22.07 | 1700000
2022-05-28 | 78420 | 78.42 | 7.39 | 7.72 | 130 | 17 | 332 | 40 | 295 | 25 | NA | 400 | 0.2 | 23.15 | 1400000
2022-05-29 | 84450 | 84.45 | 7.42 | 7.69 | 140 | 18 | 344 | 44 | 299 | 28 | NA | 500 | 0.3 | 22.15 | 1300000
2022-05-30 | 80560 | 80.56 | 7.45 | 7.65 | 135 | 19 | 336 | 40 | 311 | 26 | NA | 600 | 0.2 | 21.59 | 1400000
2022-05-31 | 78250 | 78.25 | 7.38 | 7.67 | 130 | 16 | 328 | 44 | 289 | 24 | NA | 400 | 0.2 | 22.35 | 1300000
Average | 63445.8065 | 63.4458 | 7.399 | 7.6913 | 130.6452 | 15.9032 | 331.0968 | 40.129 | 292.8065 | 25.871 | NA | 493.5484 | 0.22258 | 22.3713 | 1451612.9032
| 1966820 | 1966.82
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 17440 | 17.44 | 7.35 | 7.65 | 120 | 12 | 312 | 32 | 261 | 21 |  | 400 | 0.2 | 21.21 | 1200000
Max | 85910 | 85.91 | 7.45 | 7.73 | 140 | 19 | 348 | 48 | 315 | 29 |  | 600 | 0.3 | 23.17 | 1700000