## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 102110 | 102.11 | 7.39 | 7.74 | 135 | 29 | 325 | 46 | 299 | 43 | NA | 800 | 0.3 | 25.6 | 1400000
2023-05-02 | 114440 | 114.44 | 7.45 | 7.77 | 140 | 26 | 319 | 44 | 293 | 42 | NA | 600 | 0.2 | 25.2 | 1700000
2023-05-03 | 114340 | 114.34 | 7.42 | 7.75 | 130 | 27 | 312 | 42 | 288 | 33 | NA | 500 | 0.2 | 24.4 | 1300000
2023-05-04 | 116470 | 118.48 | 7.42 | 7.73 | 125 | 26 | 327 | 40 | 320 | 30 | NA | 700 | 0.3 | 24.7 | 1400000
2023-05-05 | 107590 | 107.59 | 7.46 | 7.76 | 135 | 28 | 310 | 43 | 290 | 37 | NA | 500 | 0.2 | 25.4 | 1300000
2023-05-06 | 101820 | 101.82 | 7.39 | 7.53 | 140 | 27 | 318 | 40 | 296 | 35 | NA | 800 | 0.3 | 25 | 1100000
2023-05-07 | 103360 | 103.36 | 7.39 | 7.57 | 145 | 29 | 340 | 42 | 306 | 40 | NA | 500 | 0.2 | 24.4 | 1700000
2023-05-08 | 101050 | 101.05 | 7.33 | 7.76 | 140 | 27 | 332 | 44 | 297 | 36 | NA | 600 | 0.3 | 24.5 | 1200000
2023-05-09 | 98290 | 98.29 | 7.39 | 7.75 | 145 | 29 | 328 | 43 | 294 | 40 | NA | 700 | 0.2 | 24.8 | 1400000
2023-05-10 | 92560 | 93.37 | 7.35 | 7.76 | 120 | 27 | 340 | 40 | 305 | 35 | NA | 800 | 0.3 | 24.6 | 1300000
2023-05-11 | 96300 | 96.3 | 7.38 | 7.72 | 145 | 28 | 344 | 44 | 292 | 37 | NA | 600 | 0.2 | 24.9 | 1400000
2023-05-12 | 94050 | 94.05 | 7.35 | 7.78 | 135 | 29 | 328 | 42 | 305 | 39 | NA | 900 | 0.3 | 25 | 1700000
2023-05-13 | 101680 | 101.68 | 7.39 | 7.79 | 140 | 30 | 336 | 44 | 298 | 36 | NA | 500 | 0.2 | 24.8 | 1300000
2023-05-14 | 99020 | 99.02 | 7.44 | 7.8 | 130 | 26 | 328 | 42 | 299 | 35 | NA | 800 | 0.3 | 24.5 | 1100000
2023-05-15 | 96560 | 96.56 | 7.43 | 7.88 | 135 | 27 | 334 | 41 | 303 | 38 | NA | 600 | 0.2 | 25 | 1400000
2023-05-16 | 97340 | 97.34 | 7.39 | 7.87 | 145 | 28 | 340 | 44 | 294 | 40 | NA | 700 | 0.3 | 24.8 | 1700000
2023-05-17 | 98280 | 98.28 | 7.41 | 7.92 | 140 | 25 | 330 | 40 | 288 | 37 | NA | 500 | 0.2 | 24.4 | 1300000
2023-05-18 | 98940 | 98.94 | 7.42 | 7.86 | 130 | 29 | 338 | 42 | 299 | 35 | NA | 600 | 0.3 | 25.1 | 1100000
2023-05-19 | 88200 | 88.2 | 7.41 | 7.82 | 145 | 30 | 340 | 40 | 305 | 34 | NA | 800 | 0.2 | 25.2 | 1200000
2023-05-20 | 94860 | 94.86 | 7.43 | 7.86 | 135 | 27 | 332 | 39 | 296 | 36 | NA | 600 | 0.2 | 24.5 | 1400000
2023-05-21 | 90980 | 90.98 | 7.33 | 7.79 | 130 | 25 | 333 | 44 | 295 | 38 | NA | 800 | 0.3 | 25.1 | 1300000
2023-05-22 | 100090 | 100.09 | 7.35 | 7.91 | 125 | 30 | 328 | 48 | 294 | 43 | NA | 700 | 0.2 | 25.09 | 1100000
2023-05-23 | 97780 | 97.78 | 7.46 | 7.83 | 135 | 30 | 336 | 45 | 309 | 39 | NA | 500 | 0.3 | 24.4 | 1400000
2023-05-24 | 101150 | 101.15 | 7.49 | 7.89 | 140 | 28 | 330 | 46 | 305 | 41 | NA | 700 | 0.3 | 24 | 1300000
2023-05-25 | 96980 | 96.98 | 7.58 | 7.93 | 135 | 30 | 324 | 45 | 303 | 40 | NA | 400 | 0.2 | 24.8 | 1100000
2023-05-26 | 106480 | 106.48 | 7.59 | 7.84 | 145 | 27 | 338 | 43 | 309 | 38 | NA | 500 | 0.3 | 24.5 | 1200000
2023-05-27 | 106910 | 106.91 | 7.31 | 7.87 | 130 | 26 | 320 | 44 | 296 | 34 | NA | 800 | 0.3 | 25.2 | 1200000
2023-05-28 | 101190 | 101.19 | 7.02 | 7.88 | 125 | 29 | 326 | 43 | 293 | 36 | NA | 600 | 0.2 | 25.2 | 1400000
2023-05-29 | 104160 | 104.16 | 7.05 | 7.94 | 140 | 25 | 334 | 42 | 293 | 37 | NA | 700 | 0.3 | 24.8 | 1100000
2023-05-30 | 104260 | 104.26 | 7.06 | 7.95 | 135 | 28 | 326 | 44 | 305 | 35 | NA | 500 | 0.2 | 25.06 | 1300000
2023-05-31 | 106870 | 106.87 | 6.97 | 7.73 | 129 | 24 | 332 | 40 | 291 | 34 | NA | 400 | 0.3 | 25 | 1700000
Average | 101100.3226 | 101.1913 | 7.3629 | 7.8058 | 135.6129 | 27.6129 | 329.9355 | 42.7742 | 298.7097 | 37.1935 | NA | 635.4839 | 0.25161 | 24.8371 | 1338709.6774
3136.93
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 88200 | 88.2 | 6.97 | 7.53 | 120 | 24 | 310 | 39 | 288 | 30 |  | 400 | 0.2 | 24 | 1100000
Max | 116470 | 118.48 | 7.59 | 7.95 | 145 | 30 | 344 | 48 | 320 | 43 |  | 900 | 0.3 | 25.6 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 75460 | 75.46 | 7.23 | 7.72 | 130 | 17 | 328 | 44 | 295 | 27 | NA | 600 | 0.3 | 24.98 | 1300000
2023-05-02 | 80060 | 80.06 | 7.32 | 7.69 | 125 | 16 | 316 | 40 | 292 | 26 | NA | 700 | 0.2 | 23.9 | 1700000
2023-05-03 | 75770 | 75.77 | 7.28 | 7.7 | 135 | 18 | 324 | 44 | 285 | 25 | NA | 500 | 0.3 | 23.78 | 1400000
2023-05-04 | 79360 | 79.36 | 7.26 | 7.69 | 125 | 17 | 312 | 40 | 291 | 26 | NA | 400 | 0.3 | 24.37 | 1300000
2023-05-05 | 79800 | 79.8 | 7.31 | 7.59 | 130 | 16 | 308 | 36 | 276 | 25 | NA | 600 | 0.2 | 23.81 | 1700000
2023-05-06 | 79380 | 79.38 | 7.24 | 7.58 | 135 | 17 | 316 | 40 | 292 | 26 | NA | 500 | 0.3 | 23.69 | 1400000
2023-05-07 | 76600 | 76.6 | 7.28 | 7.64 | 125 | 16 | 324 | 44 | 298 | 27 | NA | 700 | 0.2 | 22.95 | 1700000
2023-05-08 | 73100 | 73.1 | 7.23 | 7.62 | 130 | 17 | 312 | 40 | 287 | 25 | NA | 600 | 0.3 | 24.7 | 1400000
2023-05-09 | 71370 | 71.37 | 7.26 | 7.63 | 140 | 18 | 316 | 44 | 295 | 26 | NA | 400 | 0.2 | 23.18 | 1700000
2023-05-10 | 70200 | 70.2 | 7.31 | 7.65 | 135 | 17 | 328 | 40 | 306 | 27 | NA | 500 | 0.3 | 23.76 | 1300000
2023-05-11 | 73250 | 73.25 | 7.29 | 7.62 | 130 | 16 | 324 | 44 | 284 | 26 | NA | 600 | 0.2 | 22.92 | 1400000
2023-05-12 | 69100 | 69.1 | 7.32 | 7.68 | 140 | 17 | 312 | 40 | 279 | 25 | NA | 700 | 0.3 | 23.82 | 1700000
2023-05-13 | 71800 | 71.8 | 7.24 | 7.66 | 135 | 18 | 320 | 44 | 285 | 26 | NA | 500 | 0.2 | 23.42 | 1400000
2023-05-14 | 70350 | 70.35 | 7.29 | 7.65 | 125 | 16 | 316 | 40 | 293 | 27 | NA | 400 | 0.3 | 23.15 | 1300000
2023-05-15 | 67520 | 67.52 | 7.23 | 7.64 | 130 | 17 | 308 | 44 | 276 | 26 | NA | 600 | 0.3 | 23.34 | 1700000
2023-05-16 | 68110 | 68.11 | 7.25 | 7.62 | 135 | 18 | 324 | 40 | 288 | 27 | NA | 700 | 0.2 | 22.92 | 1400000
2023-05-17 | 71510 | 71.51 | 7.28 | 7.67 | 125 | 17 | 328 | 44 | 294 | 26 | NA | 500 | 0.3 | 23.35 | 1300000
2023-05-18 | 75160 | 75.16 | 7.26 | 7.65 | 130 | 16 | 316 | 40 | 286 | 25 | NA | 400 | 0.3 | 24.98 | 1400000
2023-05-19 | 71160 | 71.61 | 7.24 | 7.69 | 140 | 19 | 336 | 48 | 309 | 27 | NA | 600 | 0.3 | 24 | 1300000
2023-05-20 | 72770 | 72.77 | 7.27 | 7.71 | 135 | 17 | 324 | 40 | 283 | 26 | NA | 500 | 0.2 | 24.53 | 1700000
2023-05-21 | 72360 | 72.36 | 7.24 | 7.74 | 125 | 16 | 320 | 44 | 287 | 27 | NA | 600 | 0.2 | 24.98 | 1400000
2023-05-22 | 74250 | 74.25 | 7.28 | 7.72 | 130 | 17 | 328 | 40 | 293 | 26 | NA | 700 | 0.3 | 23.12 | 1700000
2023-05-23 | 72390 | 72.39 | 7.25 | 7.71 | 135 | 18 | 316 | 44 | 297 | 27 | NA | 400 | 0.3 | 23.16 | 1300000
2023-05-24 | 73230 | 73.23 | 7.29 | 7.73 | 145 | 19 | 336 | 48 | 311 | 28 | NA | 500 | 0.2 | 24.21 | 1400000
2023-05-25 | 74300 | 74.3 | 7.28 | 7.75 | 130 | 17 | 312 | 40 | 287 | 26 | NA | 700 | 0.2 | 23.82 | 1700000
2023-05-26 | 83270 | 83.27 | 7.23 | 7.76 | 140 | 18 | 324 | 44 | 276 | 25 | NA | 600 | 0.3 | 22.54 | 1300000
2023-05-27 | 81670 | 81.67 | 7.18 | 7.69 | 135 | 17 | 312 | 40 | 284 | 27 | NA | 500 | 0.3 | 24.9 | 1400000
2023-05-28 | 80370 | 80.37 | 7.26 | 7.73 | 125 | 16 | 316 | 44 | 297 | 26 | NA | 400 | 0.2 | 23.94 | 1700000
2023-05-29 | 70800 | 70.8 | 7.32 | 7.71 | 140 | 18 | 324 | 44 | 305 | 27 | NA | 600 | 0.3 | 23.44 | 1400000
2023-05-30 | 75410 | 75.41 | 7.29 | 7.73 | 130 | 17 | 328 | 40 | 291 | 26 | NA | 700 | 0.3 | 23.08 | 1700000
2023-05-31 | 68520 | 68.43 | 7.33 | 7.72 | 145 | 19 | 332 | 44 | 308 | 28 | NA | 500 | 0.2 | 24.63 | 1300000
Average | 74141.9355 | 74.1535 | 7.269 | 7.6803 | 132.7419 | 17.1613 | 320.6452 | 42.1935 | 291.2903 | 26.2581 | NA | 554.8387 | 0.25806 | 23.7861 | 1477419.3548
2298.76
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 67520 | 67.52 | 7.18 | 7.58 | 125 | 16 | 308 | 36 | 276 | 25 |  | 400 | 0.2 | 22.54 | 1300000
Max | 83270 | 83.27 | 7.33 | 7.76 | 145 | 19 | 336 | 48 | 311 | 28 |  | 700 | 0.3 | 24.98 | 1700000