## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-11-01 | 114200 | 114.2 | 7.15 | 7.69 | 140 | 22 | 316 | 42 | 282 | 36 | NA | 500 | 0.2 | 24.6 | 1700000
2023-11-02 | 111600 | 111.6 | 7.23 | 7.61 | 125 | 20 | 305 | 40 | 275 | 39 | NA | 700 | 0.3 | 23.75 | 1400000
2023-11-03 | 101580 | 101.58 | 7.28 | 7.56 | 135 | 19 | 298 | 44 | 281 | 41 | NA | 400 | 0.2 | 24.48 | 1100000
2023-11-04 | 102010 | 102.01 | 7.24 | 7.62 | 123 | 21 | 304 | 43 | 278 | 40 | NA | 600 | 0.3 | 24.13 | 1300000
2023-11-05 | 103470 | 103.47 | 7.26 | 7.56 | 140 | 23 | 311 | 46 | 271 | 42 | NA | 500 | 0.2 | 24.49 | 1200000
2023-11-06 | 107000 | 107 | 7.21 | 7.61 | 130 | 21 | 308 | 44 | 268 | 40 | NA | 700 | 0.3 | 24.9 | 1400000
2023-11-07 | 111700 | 111.7 | 7.28 | 7.56 | 135 | 20 | 312 | 42 | 284 | 40 | NA | 400 | 0.3 | 24.6 | 1100000
2023-11-08 | 113340 | 113.34 | 7.44 | 7.53 | 130 | 19 | 298 | 40 | 279 | 38 | NA | 700 | 0.2 | 24.45 | 1200000
2023-11-09 | 112810 | 112.81 | 7.62 | 7.69 | 135 | 21 | 302 | 44 | 273 | 40 | NA | 500 | 0.3 | 24.64 | 1700000
2023-11-10 | 115540 | 115.54 | 7.61 | 7.64 | 140 | 20 | 316 | 42 | 286 | 41 | NA | 600 | 0.3 | 24.54 | 1300000
2023-11-11 | 115290 | 115.29 | 7.6 | 7.61 | 130 | 19 | 308 | 46 | 280 | 42 | NA | 700 | 0.3 | 23.87 | 1200000
2023-11-12 | 119200 | 119.2 | 7.61 | 7.6 | 135 | 23 | 312 | 45 | 274 | 43 | NA | 600 | 0.3 | 24.35 | 1100000
2023-11-13 | 114190 | 114.19 | 7.68 | 7.62 | 130 | 24 | 302 | 46 | 269 | 42 | NA | 500 | 0.3 | 24.26 | 1400000
2023-11-14 | 114170 | 114.17 | 7.64 | 7.61 | 125 | 21 | 320 | 42 | 278 | 40 | NA | 400 | 0.3 | 24.16 | 1300000
2023-11-15 | 115720 | 115.72 | 7.56 | 7.59 | 135 | 21 | 300 | 44 | 273 | 38 | NA | 700 | 0.2 | 24.68 | 1700000
2023-11-16 | 115540 | 115.54 | 7.58 | 7.63 | 120 | 23 | 292 | 42 | 275 | 46 | NA | 600 | 0.3 | 24.36 | 1200000
2023-11-17 | 112960 | 112.96 | 7.57 | 7.62 | 130 | 22 | 306 | 40 | 268 | 40 | NA | 400 | 0.3 | 24.3 | 1100000
2023-11-18 | 112440 | 112.44 | 7.55 | 7.6 | 135 | 21 | 300 | 44 | 271 | 41 | NA | 500 | 0.3 | 23.9 | 1400000
2023-11-19 | 113010 | 113.01 | 7.55 | 7.65 | 140 | 23 | 308 | 45 | 276 | 39 | NA | 700 | 0.2 | 24.6 | 1300000
2023-11-20 | 115150 | 115.15 | 7.49 | 7.61 | 135 | 24 | 296 | 46 | 271 | 42 | NA | 500 | 0.3 | 23.9 | 1200000
2023-11-21 | 113900 | 113.9 | 7.43 | 7.53 | 125 | 21 | 306 | 43 | 278 | 39 | NA | 700 | 0.2 | 24.56 | 1100000
2023-11-22 | 113580 | 113.58 | 7.36 | 7.52 | 135 | 20 | 304 | 42 | 273 | 42 | NA | 600 | 0.3 | 24.36 | 1400000
2023-11-23 | 109190 | 109.19 | 7.28 | 7.56 | 140 | 21 | 308 | 40 | 275 | 41 | NA | 500 | 0.2 | 24.06 | 1400000
2023-11-24 | 112840 | 112.84 | 7.26 | 7.49 | 125 | 22 | 292 | 45 | 269 | 47 | NA | 400 | 0.3 | 24.07 | 1200000
2023-11-25 | 113100 | 113.1 | 7.3 | 7.48 | 130 | 22 | 296 | 42 | 267 | 42 | NA | 600 | 0.2 | 24.6 | 1300000
2023-11-26 | 113790 | 113.79 | 7.33 | 7.55 | 140 | 20 | 302 | 44 | 266 | 41 | NA | 500 | 0.3 | 24.2 | 1700000
2023-11-27 | 113040 | 113.04 | 7.27 | 7.62 | 135 | 25 | 308 | 46 | 270 | 44 | NA | 800 | 0.2 | 24.11 | 1200000
2023-11-28 | 112720 | 112.72 | 7.09 | 7.49 | 125 | 22 | 312 | 42 | 277 | 40 | NA | 600 | 0.3 | 24.35 | 1100000
2023-11-29 | 111630 | 111.63 | 7.07 | 7.46 | 130 | 19 | 302 | 43 | 275 | 41 | NA | 700 | 0.2 | 23.92 | 1300000
2023-11-30 | 110570 | 110.57 | 7.33 | 7.41 | 140 | 21 | 314 | 45 | 282 | 43 | NA | 600 | 0.3 | 24.68 | 1200000
Average | 112176 | 112.176 | 7.3957 | 7.5773 | 132.4333 | 21.3333 | 305.2667 | 43.3 | 274.8 | 41 | NA | 573.3333 | 0.26333 | 24.329 | 1306666.6667
3365.28
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 101580 | 101.58 | 7.07 | 7.41 | 120 | 19 | 292 | 40 | 266 | 36 |  | 400 | 0.2 | 23.75 | 1100000
Max | 119200 | 119.2 | 7.68 | 7.69 | 140 | 25 | 320 | 46 | 286 | 47 |  | 800 | 0.3 | 24.9 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-11-01 | 80890 | 80.89 | 7.23 | 7.69 | 135 | 18 | 304 | 44 | 273 | 26 | NA | 500 | 0.3 | 23.24 | 1200000
2023-11-02 | 80560 | 80.56 | 7.24 | 7.65 | 125 | 17 | 292 | 40 | 263 | 24 | NA | 600 | 0.3 | 23.69 | 1400000
2023-11-03 | 81380 | 81.38 | 7.21 | 7.67 | 130 | 18 | 288 | 48 | 261 | 25 | NA | 400 | 0.2 | 24.7 | 1300000
2023-11-04 | 78830 | 78.83 | 7.22 | 7.71 | 120 | 16 | 296 | 40 | 265 | 26 | NA | 500 | 0.3 | 23.51 | 1700000
2023-11-05 | 77670 | 77.67 | 7.23 | 7.72 | 130 | 18 | 292 | 44 | 271 | 24 | NA | 700 | 0.2 | 23.24 | 1400000
2023-11-06 | 78940 | 78.94 | 7.24 | 7.72 | 120 | 17 | 300 | 48 | 268 | 26 | NA | 600 | 0.2 | 23.18 | 1700000
2023-11-07 | 79890 | 79.89 | 7.25 | 7.74 | 125 | 16 | 288 | 40 | 267 | 24 | NA | 400 | 0.3 | 24.89 | 1300000
2023-11-08 | 80230 | 80.23 | 7.27 | 7.72 | 135 | 18 | 292 | 44 | 265 | 26 | NA | 500 | 0.3 | 23.01 | 1400000
2023-11-09 | 79220 | 79.22 | 7.28 | 7.74 | 125 | 16 | 296 | 40 | 268 | 23 | NA | 500 | 0.2 | 23.8 | 1400000
2023-11-10 | 81420 | 81.42 | 7.14 | 7.72 | 130 | 17 | 292 | 40 | 290 | 24 | NA | 600 | 0.3 | 23.15 | 1300000
2023-11-11 | 80530 | 80.53 | 7.23 | 7.72 | 125 | 16 | 292 | 44 | 271 | 25 | NA | 700 | 0.2 | 23.38 | 1700000
2023-11-12 | 80980 | 80.98 | 7.24 | 7.71 | 130 | 18 | 296 | 48 | 263 | 26 | NA | 500 | 0.3 | 24.15 | 1400000
2023-11-13 | 78960 | 78.96 | 7.26 | 7.75 | 125 | 17 | 288 | 44 | 267 | 25 | NA | 400 | 0.3 | 23.35 | 1300000
2023-11-14 | 76350 | 76.35 | 7.27 | 7.72 | 120 | 16 | 292 | 40 | 265 | 26 | NA | 600 | 0.2 | 23.9 | 1700000
2023-11-15 | 76820 | 76.82 | 7.28 | 7.76 | 125 | 16 | 288 | 44 | 263 | 23 | NA | 500 | 0.3 | 23.69 | 1300000
2023-11-16 | 76190 | 76.19 | 7.27 | 7.73 | 130 | 18 | 296 | 48 | 271 | 25 | NA | 600 | 0.3 | 22.95 | 1400000
2023-11-17 | 77350 | 77.35 | 7.28 | 7.77 | 125 | 16 | 284 | 40 | 262 | 26 | NA | 400 | 0.2 | 23.69 | 1300000
2023-11-18 | 76350 | 76.35 | 7.25 | 7.74 | 120 | 15 | 292 | 42 | 276 | 25 | NA | 600 | 0.3 | 24.17 | 1700000
2023-11-19 | 78250 | 78.25 | 7.26 | 7.75 | 125 | 16 | 296 | 44 | 265 | 27 | NA | 500 | 0.3 | 23.35 | 1400000
2023-11-20 | 77960 | 77.96 | 7.23 | 7.76 | 130 | 17 | 288 | 40 | 269 | 28 | NA | 600 | 0.3 | 24.83 | 1200000
2023-11-21 | 82640 | 82.64 | 7.24 | 7.75 | 135 | 16 | 296 | 44 | 272 | 25 | NA | 400 | 0.2 | 23.58 | 1300000
2023-11-22 | 76850 | 76.85 | 7.31 | 7.79 | 130 | 17 | 292 | 40 | 265 | 26 | NA | 500 | 0.3 | 24.68 | 1700000
2023-11-23 | 76360 | 76.36 | 7.25 | 7.78 | 135 | 18 | 284 | 44 | 259 | 25 | NA | 700 | 0.3 | 23.69 | 1400000
2023-11-24 | 74130 | 74.13 | 7.26 | 7.73 | 130 | 17 | 328 | 44 | 207 | 17 | NA | 600 | 0.3 | 24.58 | 1700000
2023-11-25 | 74810 | 74.81 | 7.28 | 7.79 | 125 | 16 | 296 | 40 | 268 | 23 | NA | 500 | 0.2 | 23.5 | 1400000
2023-11-26 | 74770 | 74.77 | 7.27 | 7.77 | 145 | 19 | 292 | 44 | 258 | 24 | NA | 400 | 0.3 | 22.8 | 1300000
2023-11-27 | 77830 | 77.83 | 7.35 | 7.68 | 120 | 16 | 276 | 40 | 281 | 25 | NA | 600 | 0.3 | 23.62 | 1400000
2023-11-28 | 77190 | 77.19 | 7.21 | 7.75 | 130 | 17 | 284 | 44 | 268 | 26 | NA | 500 | 0.3 | 23.69 | 1700000
2023-11-29 | 79200 | 79.2 | 7.22 | 7.78 | 125 | 16 | 280 | 40 | 265 | 24 | NA | 400 | 0.2 | 22.92 | 1400000
2023-11-30 | 76420 | 76.42 | 7.18 | 7.76 | 135 | 17 | 292 | 40 | 281 | 25 | NA | 600 | 0.3 | 23.61 | 1300000
Average | 78299 | 78.299 | 7.2483 | 7.7357 | 128 | 16.8333 | 292.4 | 42.7333 | 266.2333 | 24.8 | NA | 530 | 0.26667 | 23.6847 | 1436666.6667
2348.97
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 74130 | 74.13 | 7.14 | 7.65 | 120 | 15 | 276 | 40 | 207 | 17 |  | 400 | 0.2 | 22.8 | 1200000
Max | 82640 | 82.64 | 7.35 | 7.79 | 145 | 19 | 328 | 48 | 290 | 28 |  | 700 | 0.3 | 24.89 | 1700000