## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 36580 | 36.58 | 7.5 | 8.07 | 170 | 18 | 344 | 36 | 280 | 24 | NA | 400 | 0.3 | 24.04 | 1100000
2024-04-02 | 36490 | 36.49 | 7.44 | 8.08 | 165 | 17 | 356 | 32 | 266 | 25 | NA | 600 | 0.3 | 24.12 | 1400000
2024-04-03 | 33540 | 33.54 | 7.42 | 7.99 | 170 | 16 | 348 | 36 | 272 | 32 | NA | 500 | 0.3 | 23.48 | 1700000
2024-04-04 | 34170 | 34.17 | 7.5 | 7.95 | 165 | 18 | 360 | 40 | 278 | 37 | NA | 700 | 0.2 | 24.56 | 1300000
2024-04-05 | 36740 | 36.74 | 7.54 | 7.93 | 175 | 19 | 352 | 36 | 266 | 26 | NA | 500 | 0.3 | 24.11 | 1100000
2024-04-06 | 35340 | 35.34 | 7.62 | 7.94 | 185 | 18 | 368 | 40 | 281 | 25 | NA | 400 | 0.2 | 24.2 | 1200000
2024-04-07 | 36800 | 36.8 | 7.58 | 7.92 | 175 | 17 | 340 | 36 | 285 | 24 | NA | 600 | 0.3 | 23.53 | 1400000
2024-04-08 | 36610 | 36.61 | 7.52 | 7.95 | 180 | 16 | 344 | 36 | 278 | 25 | NA | 400 | 0.2 | 24.51 | 1100000
2024-04-09 | 36820 | 36.82 | 7.54 | 7.94 | 185 | 17 | 368 | 36 | 270 | 23 | NA | 500 | 0.3 | 23.9 | 1300000
2024-04-10 | 35400 | 35.4 | 7.53 | 7.95 | 180 | 16 | 344 | 32 | 281 | 24 | NA | 700 | 0.3 | 24.05 | 1700000
2024-04-11 | 37570 | 37.57 | 7.55 | 7.98 | 175 | 17 | 356 | 36 | 277 | 21 | NA | 400 | 0.2 | 24.18 | 1400000
2024-04-12 | 35440 | 35.44 | 7.53 | 7.96 | 165 | 18 | 340 | 32 | 281 | 22 | NA | 500 | 0.2 | 23.9 | 1100000
2024-04-13 | 36660 | 36.66 | 7.51 | 7.95 | 175 | 19 | 348 | 36 | 273 | 23 | NA | 600 | 0.3 | 24.41 | 1300000
2024-04-14 | 41720 | 41.72 | 7.5 | 7.9 | 185 | 18 | 368 | 32 | 275 | 22 | NA | 500 | 0.3 | 24.33 | 1700000
2024-04-15 | 37850 | 37.85 | 7.51 | 7.92 | 175 | 19 | 384 | 32 | 284 | 24 | NA | 400 | 0.2 | 23.91 | 1400000
2024-04-16 | 36060 | 36.06 | 7.68 | 7.94 | 170 | 18 | 360 | 36 | 275 | 22 | NA | 600 | 0.3 | 24.5 | 1100000
2024-04-17 | 36820 | 36.82 | 7.75 | 7.91 | 175 | 20 | 372 | 36 | 280 | 24 | NA | 400 | 0.3 | 24.86 | 1200000
2024-04-18 | 34470 | 34.47 | 7.67 | 7.92 | 170 | 19 | 364 | 32 | 272 | 25 | NA | 700 | 0.2 | 24.57 | 1400000
2024-04-19 | 35750 | 35.75 | 7.68 | 7.9 | 165 | 20 | 356 | 36 | 284 | 26 | NA | 600 | 0.3 | 23.95 | 1200000
2024-04-20 | 35730 | 35.73 | 7.72 | 7.91 | 170 | 19 | 360 | 32 | 279 | 25 | NA | 500 | 0.3 | 24.2 | 1700000
2024-04-21 | 35820 | 35.82 | 7.74 | 7.89 | 175 | 18 | 376 | 36 | 274 | 27 | NA | 600 | 0.2 | 24.31 | 1300000
2024-04-22 | 36510 | 36.51 | 7.7 | 7.93 | 170 | 17 | 364 | 32 | 281 | 25 | NA | 500 | 0.3 | 23.84 | 1100000
2024-04-23 | 36740 | 36.74 | 7.69 | 7.92 | 180 | 16 | 372 | 32 | 288 | 27 | NA | 700 | 0.3 | 24.1 | 1300000
2024-04-24 | 35930 | 35.93 | 7.67 | 7.95 | 185 | 18 | 376 | 32 | 301 | 25 | NA | 600 | 0.2 | 24.41 | 1700000
2024-04-25 | 33720 | 33.72 | 7.65 | 7.91 | 180 | 20 | 380 | 36 | 289 | 26 | NA | 500 | 0.3 | 25.1 | 1400000
2024-04-26 | 35740 | 35.74 | 7.6 | 7.92 | 185 | 21 | 384 | 36 | 285 | 27 | NA | 700 | 0.3 | 24.17 | 1200000
2024-04-27 | 35400 | 35.4 | 7.62 | 7.9 | 175 | 19 | 368 | 36 | 300 | 30 | NA | 500 | 0.2 | 24.3 | 1700000
2024-04-28 | 35240 | 35.24 | 7.64 | 7.92 | 180 | 20 | 376 | 40 | 289 | 26 | NA | 400 | 0.3 | 23.91 | 1100000
2024-04-29 | 34490 | 34.49 | 7.69 | 7.91 | 175 | 21 | 380 | 36 | 290 | 25 | NA | 500 | 0.2 | 24.19 | 1300000
2024-04-30 | 35590 | 35.59 | 7.74 | 7.94 | 180 | 20 | 368 | 40 | 272 | 26 | NA | 700 | 0.2 | 24.72 | 1700000
Average | 36058 | 36.058 | 7.601 | 7.94 | 175.3333 | 18.3 | 362.5333 | 35.2 | 280.2 | 25.4333 |  | 540 | 0.26 | 24.212 | 1353333.3333
1081.74
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33540 | 33.54 | 7.42 | 7.89 | 165 | 16 | 340 | 32 | 266 | 21 |  | 400 | 0.2 | 23.48 | 1100000
Max | 41720 | 41.72 | 7.75 | 8.08 | 185 | 21 | 384 | 40 | 301 | 37 |  | 700 | 0.3 | 25.1 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 15240 | 15.24 | 7.65 | 7.75 | 180 | 21 | 356 | 36 | 290 | 22 | NA | 600 | 0.2 | 23.21 | 1700000
2024-04-02 | 15740 | 15.74 | 7.59 | 7.75 | 170 | 19 | 340 | 36 | 280 | 22 | NA | 500 | 0.2 | 23.51 | 1400000
2024-04-03 | 16210 | 16.21 | 7.42 | 7.73 | 170 | 20 | 336 | 40 | 280 | 19 | NA | 400 | 0.3 | 22.17 | 1300000
2024-04-04 | 16640 | 16.64 | 7.31 | 7.76 | 160 | 20 | 312 | 36 | 288 | 20 | NA | 600 | 0.2 | 23.53 | 1700000
2024-04-05 | 17790 | 17.79 | 7.52 | 7.77 | 165 | 19 | 320 | 40 | 275 | 18 | NA | 400 | 0.3 | 24.22 | 1300000
2024-04-06 | 16090 | 16.09 | 7.47 | 7.74 | 160 | 19 | 324 | 36 | 273 | 21 | NA | 500 | 0.2 | 24.29 | 1700000
2024-04-07 | 16540 | 16.54 | 7.41 | 7.74 | 165 | 20 | 328 | 36 | 294 | 20 | NA | 600 | 0.2 | 24.29 | 1700000
2024-04-08 | 15920 | 15.92 | 7.3 | 7.77 | 160 | 20 | 316 | 40 | 280 | 24 | NA | 400 | 0.3 | 23.41 | 1300000
2024-04-09 | 16470 | 16.47 | 7.14 | 7.79 | 160 | 19 | 320 | 36 | 290 | 22 | NA | 500 | 0.2 | 24.24 | 1700000
2024-04-10 | 16820 | 16.82 | 7.29 | 7.77 | 155 | 20 | 308 | 40 | 280 | 19 | NA | 600 | 0.3 | 24.12 | 1400000
2024-04-11 | 17190 | 17.19 | 7.56 | 7.8 | 160 | 19 | 316 | 36 | 270 | 20 | NA | 500 | 0.2 | 23.09 | 1700000
2024-04-12 | 17960 | 17.96 | 7.7 | 7.79 | 160 | 20 | 316 | 36 | 271 | 18 | NA | 600 | 0.2 | 23.58 | 1700000
2024-04-13 | 15520 | 15.52 | 7.66 | 7.79 | 165 | 21 | 308 | 40 | 270 | 20 | NA | 400 | 0.3 | 23.09 | 1300000
2024-04-14 | 17490 | 17.49 | 7.53 | 7.8 | 165 | 20 | 320 | 40 | 280 | 25 | NA | 600 | 0.2 | 24.07 | 1700000
2024-04-15 | 16670 | 16.67 | 7.53 | 7.78 | 160 | 21 | 328 | 36 | 300 | 27 | NA | 500 | 0.2 | 22.18 | 1400000
2024-04-16 | 16440 | 16.44 | 7.52 | 7.79 | 165 | 22 | 316 | 40 | 302 | 24 | NA | 600 | 0.3 | 23.93 | 1700000
2024-04-17 | 16390 | 16.39 | 7.56 | 7.81 | 160 | 20 | 324 | 36 | 280 | 21 | NA | 500 | 0.2 | 22.12 | 1300000
2024-04-18 | 15300 | 15.3 | 7.5 | 7.81 | 160 | 20 | 356 | 36 | 280 | 19 | NA | 400 | 0.3 | 23.19 | 1300000
2024-04-19 | 15640 | 15.64 | 7.31 | 7.82 | 155 | 20 | 308 | 40 | 264 | 18 | NA | 600 | 0.2 | 23.58 | 1700000
2024-04-20 | 15820 | 15.82 | 7.25 | 7.83 | 160 | 21 | 320 | 36 | 280 | 20 | NA | 500 | 0.2 | 23.23 | 1400000
2024-04-21 | 16480 | 16.48 | 7.3 | 7.82 | 165 | 22 | 316 | 36 | 275 | 22 | NA | 400 | 0.3 | 24.12 | 1300000
2024-04-22 | 15580 | 15.58 | 7.36 | 7.8 | 160 | 21 | 328 | 40 | 302 | 22 | NA | 600 | 0.2 | 23.12 | 1700000
2024-04-23 | 15860 | 15.86 | 7.46 | 7.82 | 155 | 20 | 308 | 40 | 310 | 23 | NA | 400 | 0.3 | 22.13 | 1300000
2024-04-24 | 16250 | 16.25 | 7.47 | 7.8 | 160 | 20 | 320 | 44 | 320 | 24 | NA | 400 | 0.3 | 21.29 | 1700000
2024-04-25 | 16010 | 16.01 | 7.36 | 7.83 | 165 | 21 | 308 | 40 | 305 | 23 | NA | 600 | 0.2 | 24.07 | 1700000
2024-04-26 | 16880 | 16.88 | 7.53 | 7.81 | 165 | 20 | 324 | 40 | 300 | 20 | NA | 400 | 0.3 | 23.15 | 1300000
2024-04-27 | 15960 | 15.96 | 7.61 | 7.83 | 170 | 22 | 332 | 44 | 310 | 19 | NA | 500 | 0.2 | 24.12 | 1400000
2024-04-28 | 16570 | 16.57 | 7.46 | 7.79 | 175 | 21 | 336 | 40 | 315 | 24 | NA | 400 | 0.3 | 23.23 | 1300000
2024-04-29 | 15820 | 15.82 | 7.49 | 7.81 | 160 | 20 | 320 | 44 | 260 | 20 | NA | 600 | 0.2 | 23.25 | 1700000
2024-04-30 | 16500 | 16.5 | 7.56 | 7.82 | 165 | 21 | 316 | 40 | 270 | 21 | NA | 500 | 0.2 | 24.12 | 1400000
Average | 16326.3333 | 16.3263 | 7.4607 | 7.7907 | 163.1667 | 20.3 | 322.6667 | 38.6667 | 286.4667 | 21.2333 |  | 503.3333 | 0.24 | 23.3883 | 1506666.6667
489.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 15240 | 15.24 | 7.14 | 7.73 | 155 | 19 | 308 | 36 | 260 | 18 |  | 400 | 0.2 | 21.29 | 1300000
Max | 17960 | 17.96 | 7.7 | 7.83 | 180 | 22 | 356 | 44 | 320 | 27 |  | 600 | 0.3 | 24.29 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 10610 | 10.61 | 7.76 | 7.64 | 165 | 14 | 344 | 36 | 290 | 17 | NA | 700 | 0.3 | 23.57 | 1400000 | From 01.04.2024 to 04.04.2024: 1. Sewage from 13 I&Ds is coming into SPS. 2. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 3. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-04-02 | 11220 | 11.22 | 7.64 | 7.57 | 160 | 16 | 336 | 40 | 306 | 20 | NA | 600 | 0.2 | 24.48 | 1100000
2024-04-03 | 11280 | 11.28 | 7.71 | 7.65 | 155 | 15 | 340 | 36 | 297 | 19 | NA | 500 | 0.3 | 24.06 | 1200000
2024-04-04 | 10400 | 10.4 | 7.74 | 7.57 | 160 | 16 | 336 | 44 | 286 | 21 | NA | 600 | 0.3 | 23.36 | 1300000
2024-04-05 | 12000 | 12 | 7.72 | 7.67 | 155 | 15 | 344 | 40 | 280 | 19 | NA | 700 | 0.3 | 23.19 | 1400000 | From 05.04.2024 to 30.04.2024: 1. Sewage from 12 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla is dismantled 0n 05.04.2024 and sewage is not coming to Shastri Bridge SPS. 3. Due to various issues in I&Ds, Trunk Sewer and overflow at one newly constructed manhole, sewage received from tapped I&Ds is less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-04-06 | 12070 | 12.07 | 7.79 | 7.69 | 165 | 14 | 340 | 44 | 307 | 17 | NA | 400 | 0.2 | 24.51 | 1100000
2024-04-07 | 11380 | 11.38 | 7.6 | 7.65 | 160 | 16 | 336 | 40 | 303 | 18 | NA | 500 | 0.2 | 23.27 | 1200000
2024-04-08 | 11320 | 11.32 | 7.48 | 7.55 | 155 | 14 | 340 | 36 | 290 | 17 | NA | 600 | 0.2 | 23.79 | 1100000
2024-04-09 | 11400 | 11.4 | 7.74 | 7.7 | 160 | 15 | 332 | 40 | 295 | 19 | NA | 400 | 0.3 | 24.12 | 1200000
2024-04-10 | 11520 | 11.52 | 7.81 | 7.72 | 165 | 16 | 328 | 44 | 287 | 18 | NA | 500 | 0.3 | 24.07 | 1400000
2024-04-11 | 11560 | 11.56 | 7.75 | 7.59 | 155 | 14 | 336 | 36 | 292 | 17 | NA | 700 | 0.3 | 23.78 | 1200000
2024-04-12 | 10770 | 10.77 | 7.77 | 7.61 | 160 | 16 | 340 | 44 | 304 | 18 | NA | 600 | 0.3 | 24.17 | 1400000
2024-04-13 | 10250 | 10.25 | 7.79 | 7.51 | 165 | 15 | 344 | 36 | 286 | 19 | NA | 500 | 0.2 | 23.46 | 1100000
2024-04-14 | 10970 | 10.97 | 7.82 | 7.7 | 160 | 14 | 336 | 40 | 290 | 17 | NA | 400 | 0.2 | 23.93 | 1200000
2024-04-15 | 10700 | 10.7 | 7.88 | 7.73 | 165 | 15 | 344 | 36 | 297 | 18 | NA | 600 | 0.3 | 24.28 | 1700000
2024-04-16 | 10700 | 10.7 | 7.76 | 7.59 | 160 | 14 | 340 | 40 | 288 | 17 | NA | 500 | 0.2 | 22.97 | 1400000
2024-04-17 | 11080 | 11.08 | 7.74 | 7.53 | 165 | 15 | 344 | 36 | 290 | 19 | NA | 400 | 0.3 | 23.58 | 1200000
2024-04-18 | 11900 | 11.9 | 7.81 | 7.63 | 155 | 14 | 336 | 40 | 288 | 18 | NA | 700 | 0.3 | 24.11 | 1300000
2024-04-19 | 11340 | 11.34 | 7.78 | 7.54 | 160 | 16 | 328 | 44 | 320 | 17 | NA | 600 | 0.2 | 23.85 | 1100000
2024-04-20 | 11970 | 11.97 | 7.71 | 7.69 | 165 | 14 | 336 | 40 | 318 | 19 | NA | 400 | 0.2 | 24.08 | 1400000
2024-04-21 | 11290 | 11.29 | 7.77 | 7.74 | 155 | 13 | 340 | 40 | 290 | 20 | NA | 700 | 0.3 | 24.73 | 1200000
2024-04-22 | 11410 | 11.41 | 7.85 | 7.71 | 160 | 15 | 328 | 36 | 287 | 19 | NA | 600 | 0.3 | 23.59 | 1300000
2024-04-23 | 11300 | 11.3 | 7.75 | 7.69 | 165 | 14 | 344 | 40 | 310 | 17 | NA | 500 | 0.3 | 23.76 | 1400000
2024-04-24 | 10950 | 10.95 | 7.79 | 7.63 | 155 | 15 | 340 | 36 | 290 | 18 | NA | 400 | 0.2 | 24.18 | 1700000
2024-04-25 | 11000 | 11 | 7.7 | 7.65 | 160 | 14 | 336 | 36 | 306 | 19 | NA | 500 | 0.3 | 23.88 | 1300000
2024-04-26 | 11300 | 11.3 | 7.8 | 7.69 | 155 | 15 | 340 | 40 | 310 | 17 | NA | 600 | 0.3 | 23.28 | 1400000
2024-04-27 | 10610 | 10.61 | 7.83 | 7.7 | 165 | 14 | 344 | 36 | 316 | 18 | NA | 700 | 0.3 | 24.1 | 1100000
2024-04-28 | 10450 | 10.45 | 7.79 | 7.69 | 160 | 15 | 348 | 40 | 295 | 19 | NA | 500 | 0.2 | 24.78 | 1700000
2024-04-29 | 10300 | 10.3 | 7.81 | 7.65 | 155 | 14 | 340 | 36 | 286 | 18 | NA | 600 | 0.2 | 23.88 | 1200000
2024-04-30 | 10060 | 10.06 | 7.78 | 7.68 | 165 | 15 | 336 | 40 | 306 | 17 | NA | 400 | 0.3 | 24.26 | 1400000
Average | 11103.6667 | 11.1037 | 7.7557 | 7.6453 | 160.1667 | 14.7333 | 338.5333 | 39.0667 | 297 | 18.2 |  | 546.6667 | 0.26 | 23.9023 | 1303333.3333
333.11
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10060 | 10.06 | 7.48 | 7.51 | 155 | 13 | 328 | 36 | 280 | 17 |  | 400 | 0.2 | 22.97 | 1100000
Max | 12070 | 12.07 | 7.88 | 7.74 | 165 | 16 | 348 | 44 | 320 | 21 |  | 700 | 0.3 | 24.78 | 1700000