## Naini 2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 46760 | 46.77 | 7.5 | 7.7 | 185 | 20 | 344 | 40 | 278 | 20 | NA | 400 | 0.2 | 24.7 | 1200000
2023-08-02 | 49170 | 49.17 | 7.41 | 7.74 | 180 | 19 | 332 | 44 | 290 | 25 | NA | 500 | 0.3 | 25.2 | 1400000
2023-08-03 | 71730 | 71.73 | 7.4 | 7.6 | 185 | 18 | 340 | 44 | 294 | 43 | NA | 800 | 0.3 | 25.4 | 1700000
2023-08-04 | 52310 | 52.31 | 7.37 | 7.61 | 170 | 17 | 320 | 40 | 277 | 31 | NA | 700 | 0.2 | 24.9 | 1300000
2023-08-05 | 47520 | 47.52 | 7.39 | 7.71 | 175 | 18 | 324 | 36 | 302 | 24 | NA | 500 | 0.3 | 23.8 | 1700000
2023-08-06 | 44290 | 44.29 | 7.51 | 7.86 | 185 | 17 | 348 | 32 | 304 | 25 | NA | 600 | 0.3 | 25.1 | 1400000
2023-08-07 | 45410 | 45.14 | 7.22 | 7.8 | 175 | 16 | 332 | 32 | 284 | 21 | NA | 400 | 0.2 | 24.5 | 1200000
2023-08-08 | 44190 | 44.19 | 7.47 | 7.81 | 155 | 20 | 312 | 40 | 280 | 20 | NA | 500 | 0.3 | 25.7 | 1100000
2023-08-09 | 44120 | 44.12 | 7.62 | 7.86 | 180 | 23 | 320 | 48 | 274 | 19 | NA | 700 | 0.3 | 25.9 | 1400000
2023-08-10 | 44280 | 44.28 | 7.52 | 7.88 | 185 | 25 | 360 | 48 | 276 | 16 | NA | 400 | 0.2 | 24.6 | 1200000
2023-08-11 | 43440 | 43.44 | 7.39 | 7.8 | 170 | 21 | 348 | 44 | 268 | 17 | NA | 600 | 0.3 | 23.59 | 1700000
2023-08-12 | 43350 | 43.35 | 7.46 | 7.88 | 165 | 25 | 324 | 48 | 272 | 23 | NA | 500 | 0.2 | 24.12 | 1300000
2023-08-13 | 45680 | 45.68 | 7.49 | 7.9 | 170 | 24 | 332 | 44 | 300 | 24 | NA | 700 | 0.3 | 25.98 | 1100000
2023-08-14 | 46100 | 46.1 | 7.53 | 7.92 | 165 | 25 | 340 | 48 | 294 | 25 | NA | 600 | 0.2 | 25.07 | 1400000
2023-08-15 | 46540 | 46.54 | 7.5 | 7.88 | 170 | 24 | 320 | 44 | 273 | 24 | NA | 400 | 0.3 | 24.5 | 1200000
2023-08-16 | 44540 | 44.54 | 7.49 | 7.89 | 165 | 25 | 328 | 48 | 280 | 26 | NA | 500 | 0.3 | 25.04 | 1400000
2023-08-17 | 39330 | 39.33 | 7.54 | 7.87 | 160 | 21 | 312 | 40 | 287 | 20 | NA | 400 | 0.2 | 24.43 | 1700000
2023-08-18 | 45480 | 45.48 | 7.45 | 7.84 | 165 | 23 | 316 | 44 | 285 | 23 | NA | 600 | 0.3 | 25.34 | 1200000
2023-08-19 | 43190 | 43.19 | 7.49 | 7.9 | 160 | 24 | 312 | 48 | 291 | 25 | NA | 700 | 0.2 | 24.7 | 1400000
2023-08-20 | 43440 | 43.44 | 7.53 | 7.92 | 165 | 25 | 324 | 44 | 301 | 24 | NA | 500 | 0.3 | 25.17 | 1700000
2023-08-21 | 47120 | 47.12 | 7.64 | 7.87 | 155 | 24 | 308 | 48 | 283 | 26 | NA | 600 | 0.3 | 24.3 | 1200000
2023-08-22 | 51120 | 51.41 | 7.51 | 7.83 | 160 | 25 | 312 | 48 | 293 | 27 | NA | 700 | 0.2 | 25.34 | 1100000
2023-08-23 | 77600 | 77.6 | 7.38 | 7.64 | 165 | 26 | 300 | 49 | 287 | 31 | NA | 400 | 0.3 | 24.51 | 1300000
2023-08-24 | 54530 | 54.53 | 7.34 | 7.69 | 155 | 22 | 296 | 40 | 263 | 17 | NA | 500 | 0.3 | 25.4 | 1200000
2023-08-25 | 68490 | 68.49 | 7.4 | 7.7 | 165 | 23 | 308 | 46 | 270 | 29 | NA | 700 | 0.2 | 24.53 | 1400000
2023-08-26 | 55530 | 55.35 | 7.46 | 7.73 | 160 | 25 | 314 | 44 | 286 | 21 | NA | 600 | 0.2 | 24.1 | 1100000
2023-08-27 | 48100 | 48.1 | 7.6 | 7.81 | 165 | 24 | 302 | 46 | 268 | 22 | NA | 500 | 0.3 | 24.57 | 1700000
2023-08-28 | 47850 | 47.85 | 7.63 | 7.78 | 170 | 23 | 322 | 48 | 280 | 25 | NA | 400 | 0.3 | 25.11 | 1200000
2023-08-29 | 45780 | 45.78 | 7.54 | 7.83 | 185 | 24 | 342 | 45 | 306 | 22 | NA | 600 | 0.2 | 25.4 | 1400000
2023-08-30 | 46180 | 46.18 | 7.57 | 7.84 | 180 | 25 | 350 | 46 | 287 | 21 | NA | 500 | 0.3 | 24.9 | 1700000
2023-08-31 | 44100 | 44.1 | 7.53 | 7.9 | 175 | 24 | 358 | 48 | 294 | 20 | NA | 600 | 0.3 | 25.54 | 1300000
Average | 48944.1935 | 48.9394 | 7.48 | 7.8061 | 169.8387 | 22.4194 | 325.8065 | 44 | 284.7419 | 23.7419 | NA | 551.6129 | 0.26129 | 24.8852 | 1364516.129
1517.12
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 39330 | 39.33 | 7.22 | 7.6 | 155 | 16 | 296 | 32 | 263 | 16 |  | 400 | 0.2 | 23.59 | 1100000
Max | 77600 | 77.6 | 7.64 | 7.92 | 185 | 26 | 360 | 49 | 306 | 43 |  | 800 | 0.3 | 25.98 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 12740 | 12.74 | 7.63 | 7.75 | 170 | 23 | 360 | 44 | 312 | 15 | NA | 700 | 0.2 | 24.44 | 1400000 | Due to breakage of retaining wall at I&D of Basna Nalla SPS, raw sewage received at Phaphamau STP is less
2023-08-02 | 16130 | 16.13 | 7.53 | 7.67 | 165 | 22 | 364 | 44 | 355 | 14 | NA | 400 | 0.3 | 23.92 | 1300000
2023-08-03 | 13030 | 13.03 | 7.57 | 7.6 | 160 | 18 | 324 | 40 | 330 | 18 | NA | 700 | 0.2 | 24.19 | 1300000
2023-08-04 | 14070 | 14.07 | 7.51 | 7.55 | 155 | 22 | 360 | 44 | 342 | 12 | NA | 500 | 0.3 | 23.03 | 1700000
2023-08-05 | 13600 | 13.6 | 7.54 | 7.56 | 170 | 19 | 364 | 44 | 340 | 11 | NA | 700 | 0.2 | 24.58 | 1400000
2023-08-06 | 13170 | 13.17 | 7.55 | 7.63 | 180 | 21 | 368 | 48 | 336 | 9 | NA | 400 | 0.3 | 24.53 | 1300000
2023-08-07 | 12330 | 12.33 | 7.65 | 7.63 | 180 | 22 | 372 | 44 | 325 | 10 | NA | 700 | 0.2 | 22.33 | 1700000
2023-08-08 | 12030 | 12.03 | 7.66 | 7.74 | 185 | 24 | 368 | 40 | 310 | 12 | NA | 400 | 0.3 | 23.74 | 1400000 | Due to flood, pumping from Basna Nalla SPS is stopped at 4 PM on 07.08.2023
2023-08-09 | 11400 | 11.4 | 7.73 | 8.2 | 185 | 22 | 364 | 36 | 315 | 16 | NA | 600 | 0.2 | 24.9 | 1700000 | Due to flood, pumping from Basna Nalla SPS is stopped.
2023-08-10 | 11710 | 11.71 | 7.74 | 7.73 | 165 | 18 | 360 | 32 | 305 | 23 | NA | 400 | 0.3 | 23.21 | 1400000 | Since the water receded in river Ganga, pumping from Basna Nalla SPS started at 5:25 PM on 10.08.2023
2023-08-11 | 12020 | 12.02 | 7.78 | 7.76 | 170 | 16 | 368 | 28 | 315 | 24 | NA | 700 | 0.2 | 23.97 | 1700000 | Due to breakage of retaining wall at I&D of Basna Nalla SPS, raw sewage received at Phaphamau STP is less
2023-08-12 | 12070 | 12.07 | 7.76 | 7.79 | 165 | 18 | 360 | 32 | 320 | 28 | NA | 400 | 0.3 | 23.51 | 1300000
2023-08-13 | 12360 | 12.36 | 7.71 | 7.81 | 170 | 17 | 368 | 32 | 320 | 25 | NA | 600 | 0.2 | 24.23 | 1400000
2023-08-14 | 11990 | 11.99 | 7.83 | 7.85 | 175 | 18 | 364 | 32 | 298 | 26 | NA | 600 | 0.3 | 23.74 | 1700000
2023-08-15 | 12240 | 12.24 | 7.82 | 7.88 | 180 | 17 | 360 | 32 | 302 | 23 | NA | 500 | 0.2 | 24.53 | 1300000
2023-08-16 | 12660 | 12.66 | 7.81 | 7.9 | 185 | 18 | 368 | 32 | 347 | 20 | NA | 400 | 0.3 | 23.25 | 1400000
2023-08-17 | 14010 | 14.01 | 7.79 | 7.91 | 180 | 17 | 372 | 36 | 345 | 22 | NA | 600 | 0.2 | 22.85 | 1700000
2023-08-18 | 12200 | 12.2 | 7.77 | 7.83 | 150 | 18 | 330 | 34 | 339 | 24 | NA | 500 | 0.3 | 23.57 | 1300000
2023-08-19 | 11570 | 11.57 | 7.73 | 7.87 | 155 | 17 | 340 | 32 | 302 | 32 | NA | 400 | 0.3 | 22.47 | 1400000
2023-08-20 | 12680 | 12.68 | 7.71 | 7.86 | 160 | 19 | 354 | 36 | 295 | 33 | NA | 500 | 0.2 | 23.61 | 1300000
2023-08-21 | 13710 | 13.71 | 7.65 | 7.84 | 150 | 18 | 334 | 34 | 281 | 29 | NA | 600 | 0.3 | 24.17 | 1700000
2023-08-22 | 14750 | 14.75 | 7.69 | 7.81 | 155 | 19 | 324 | 32 | 309 | 26 | NA | 400 | 0.2 | 23.87 | 1400000
2023-08-23 | 17380 | 17.38 | 7.53 | 7.58 | 150 | 18 | 318 | 36 | 315 | 25 | NA | 500 | 0.3 | 21.92 | 1300000
2023-08-24 | 17800 | 17.8 | 7.56 | 7.63 | 160 | 21 | 304 | 34 | 295 | 32 | NA | 700 | 0.2 | 23.87 | 1400000
2023-08-25 | 16140 | 16.14 | 7.6 | 7.71 | 155 | 19 | 312 | 36 | 335 | 24 | NA | 500 | 0.3 | 24.13 | 1700000
2023-08-26 | 14170 | 14.17 | 7.45 | 7.57 | 175 | 20 | 344 | 34 | 329 | 21 | NA | 600 | 0.3 | 23.56 | 1300000
2023-08-27 | 14010 | 14.01 | 7.41 | 7.61 | 150 | 18 | 336 | 36 | 317 | 28 | NA | 500 | 0.2 | 23.79 | 1400000
2023-08-28 | 13670 | 13.67 | 7.58 | 7.76 | 160 | 22 | 324 | 34 | 308 | 27 | NA | 400 | 0.2 | 22.35 | 1300000
2023-08-29 | 15230 | 15.23 | 7.72 | 7.86 | 165 | 24 | 344 | 36 | 302 | 24 | NA | 500 | 0.3 | 23.16 | 1700000
2023-08-30 | 14590 | 14.59 | 7.76 | 7.84 | 175 | 22 | 340 | 38 | 315 | 22 | NA | 600 | 0.2 | 22.94 | 1400000
2023-08-31 | 14030 | 14.03 | 7.79 | 7.87 | 180 | 20 | 356 | 36 | 322 | 18 | NA | 400 | 0.3 | 23.36 | 1300000
Average | 13531.9355 | 13.5319 | 7.6632 | 7.7613 | 167.0968 | 19.5806 | 349.1613 | 36.3871 | 318.7419 | 21.7097 | NA | 529.0323 | 0.25161 | 23.6039 | 1451612.9032
419.49
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11400 | 11.4 | 7.41 | 7.55 | 150 | 16 | 304 | 28 | 281 | 9 |  | 400 | 0.2 | 21.92 | 1300000
Max | 17800 | 17.8 | 7.83 | 8.2 | 185 | 24 | 372 | 48 | 355 | 33 |  | 700 | 0.3 | 24.9 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 17130 | 17.13 | 7.24 | 7.49 | 85 | 19 | 228 | 32 | 217 | 15 | NA | 500 | 0.3 | 22.84 | 1400000 | From 01.08.2023 to 04.08.2023: 1. As I&D of Lakkar Nalla & Havelia Nalla are broken due to flood, sewage from these two nallas is not coming to Shastri Bridge SPS. 2. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-08-02 | 16790 | 16.79 | 7.31 | 7.53 | 75 | 18 | 224 | 30 | 227 | 16 | NA | 400 | 0.2 | 22.53 | 1300000
2023-08-03 | 16920 | 16.92 | 7.14 | 7.32 | 80 | 28 | 164 | 82 | 136 | 41 | NA | 500 | 0.3 | 23.14 | 1700000
2023-08-04 | 16670 | 16.67 | 7.11 | 7.29 | 85 | 29 | 158 | 78 | 127 | 38 | NA | 600 | 0.3 | 22.31 | 1400000
2023-08-05 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | From 05.08.2023 to 31.08.2023: Plant is under shutdown due to flood
2023-08-06 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-07 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-08 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-09 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-10 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-11 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-12 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-13 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-14 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-15 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-16 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-17 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-18 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-19 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-20 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-21 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-22 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-23 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-24 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-25 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-26 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-27 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-28 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-29 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-08-31 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
Average | 2177.7419 | 2.1777 | 7.2 | 7.4075 | 81.25 | 23.5 | 193.5 | 55.5 | 176.75 | 27.5 | NA | 500 | 0.275 | 22.705 | 1450000
67.51
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.11 | 7.29 | 75 | 18 | 158 | 30 | 127 | 15 |  | 400 | 0.2 | 22.31 | 1300000
Max | 17130 | 17.13 | 7.31 | 7.53 | 85 | 29 | 228 | 82 | 227 | 41 |  | 600 | 0.3 | 23.14 | 1700000