## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 41200 | 41.2 | 7.75 | 7.94 | 180 | 27 | 352 | 49 | 278 | 28 | NA | 500 | 0.3 | 24.4 | 1100000
2023-12-02 | 37620 | 37.62 | 7.67 | 7.98 | 190 | 28 | 380 | 44 | 276 | 27 | NA | 400 | 0.2 | 24.1 | 1300000
2023-12-03 | 41700 | 41.7 | 7.78 | 7.92 | 185 | 25 | 386 | 40 | 268 | 27 | NA | 400 | 0.3 | 24.62 | 1200000
2023-12-04 | 41330 | 41.33 | 7.93 | 7.97 | 190 | 26 | 372 | 44 | 282 | 23 | NA | 500 | 0.3 | 24.23 | 1400000
2023-12-05 | 38500 | 38.5 | 7.94 | 7.98 | 195 | 25 | 374 | 44 | 280 | 25 | NA | 400 | 0.2 | 24.46 | 1300000
2023-12-06 | 38000 | 38 | 7.92 | 7.95 | 190 | 26 | 380 | 45 | 276 | 20 | NA | 600 | 0.3 | 24.64 | 1700000
2023-12-07 | 43800 | 43.8 | 7.93 | 7.99 | 195 | 27 | 392 | 48 | 280 | 22 | NA | 400 | 0.3 | 24.4 | 1200000
2023-12-08 | 39640 | 39.64 | 7.91 | 7.96 | 195 | 26 | 388 | 48 | 257 | 22 | NA | 500 | 0.2 | 24.31 | 1300000
2023-12-09 | 39690 | 39.69 | 7.9 | 7.97 | 185 | 25 | 372 | 44 | 298 | 25 | NA | 600 | 0.2 | 24.4 | 1700000
2023-12-10 | 38440 | 38.44 | 7.81 | 7.93 | 180 | 26 | 364 | 48 | 291 | 26 | NA | 400 | 0.2 | 25.12 | 1300000
2023-12-11 | 38970 | 38.97 | 7.88 | 7.95 | 175 | 24 | 344 | 44 | 287 | 19 | NA | 500 | 0.3 | 23.87 | 1100000
2023-12-12 | 36920 | 36.92 | 7.8 | 7.96 | 170 | 22 | 328 | 40 | 290 | 33 | NA | 700 | 0.2 | 23.89 | 1400000
2023-12-13 | 37440 | 37.44 | 7.81 | 7.94 | 175 | 23 | 332 | 44 | 281 | 29 | NA | 600 | 0.2 | 24.1 | 1200000
2023-12-14 | 38480 | 38.48 | 7.88 | 7.99 | 170 | 22 | 328 | 40 | 267 | 24 | NA | 400 | 0.3 | 23.61 | 1400000
2023-12-15 | 38900 | 38.9 | 7.89 | 7.97 | 165 | 23 | 320 | 44 | 276 | 33 | NA | 700 | 0.2 | 24.31 | 1700000
2023-12-16 | 37880 | 37.88 | 7.9 | 7.98 | 160 | 22 | 336 | 48 | 280 | 23 | NA | 500 | 0.3 | 23.41 | 1100000
2023-12-17 | 37680 | 37.68 | 7.94 | 7.99 | 170 | 23 | 332 | 44 | 276 | 26 | NA | 600 | 0.2 | 24.13 | 1300000
2023-12-18 | 38680 | 38.68 | 7.98 | 7.99 | 175 | 22 | 328 | 48 | 284 | 25 | NA | 700 | 0.3 | 23.55 | 1700000
2023-12-19 | 37430 | 37.43 | 7.88 | 7.91 | 170 | 21 | 340 | 44 | 289 | 24 | NA | 500 | 0.3 | 23.4 | 1400000
2023-12-20 | 36880 | 36.88 | 7.73 | 7.84 | 165 | 23 | 328 | 48 | 278 | 26 | NA | 400 | 0.2 | 24.21 | 1200000
2023-12-21 | 35690 | 35.69 | 7.7 | 7.93 | 160 | 24 | 320 | 44 | 264 | 25 | NA | 500 | 0.2 | 24.19 | 1100000
2023-12-22 | 38130 | 38.13 | 7.7 | 7.87 | 170 | 25 | 340 | 44 | 290 | 26 | NA | 400 | 0.3 | 23.81 | 1400000
2023-12-23 | 38420 | 38.42 | 7.71 | 7.82 | 185 | 24 | 352 | 48 | 301 | 32 | NA | 600 | 0.3 | 24.07 | 1700000
2023-12-24 | 39250 | 39.25 | 7.68 | 7.8 | 180 | 25 | 344 | 44 | 304 | 30 | NA | 500 | 0.2 | 24.51 | 1300000
2023-12-25 | 38110 | 38.11 | 7.7 | 7.85 | 175 | 24 | 356 | 48 | 290 | 28 | NA | 700 | 0.3 | 23.87 | 1700000
2023-12-26 | 38560 | 38.56 | 7.64 | 7.81 | 185 | 25 | 340 | 44 | 300 | 27 | NA | 500 | 0.2 | 23.45 | 1400000
2023-12-27 | 39530 | 39.53 | 7.61 | 7.84 | 175 | 22 | 316 | 40 | 296 | 20 | NA | 400 | 0.2 | 24.17 | 1300000
2023-12-28 | 37530 | 37.53 | 7.54 | 7.79 | 165 | 23 | 300 | 44 | 279 | 20 | NA | 500 | 0.3 | 22.75 | 1700000
2023-12-29 | 37700 | 37.7 | 7.52 | 7.78 | 160 | 22 | 296 | 48 | 271 | 22 | NA | 600 | 0.3 | 23.67 | 1400000
2023-12-30 | 36070 | 36.07 | 7.4 | 7.75 | 155 | 24 | 312 | 40 | 280 | 24 | NA | 700 | 0.3 | 24.05 | 1100000
2023-12-31 | 39190 | 39.19 | 7.51 | 7.8 | 160 | 22 | 304 | 44 | 267 | 23 | NA | 400 | 0.2 | 24.31 | 1400000
Average | 38624.5161 | 38.6245 | 7.7723 | 7.9081 | 175.8065 | 24.0645 | 343.7419 | 44.7097 | 281.8065 | 25.2903 |  | 519.3548 | 0.25161 | 24.0648 | 1370967.7419
1197.36
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35690 | 35.69 | 7.4 | 7.75 | 155 | 21 | 296 | 40 | 257 | 19 |  | 400 | 0.2 | 22.75 | 1100000
Max | 43800 | 43.8 | 7.98 | 7.99 | 195 | 28 | 392 | 49 | 304 | 33 |  | 700 | 0.3 | 25.12 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 14670 | 14.67 | 7.23 | 7.87 | 155 | 19 | 300 | 40 | 250 | 27 | NA | 500 | 0.2 | 23.03 | 1400000
2023-12-02 | 14580 | 14.58 | 7.16 | 7.89 | 160 | 20 | 304 | 36 | 220 | 20 | NA | 400 | 0.3 | 24.53 | 1300000
2023-12-03 | 15670 | 15.67 | 7.19 | 7.89 | 165 | 19 | 308 | 40 | 250 | 28 | NA | 600 | 0.3 | 24.29 | 1700000
2023-12-04 | 14000 | 14 | 7.23 | 7.87 | 160 | 20 | 316 | 36 | 242 | 27 | NA | 400 | 0.2 | 23.9 | 1300000
2023-12-05 | 16080 | 16.08 | 7.3 | 7.91 | 155 | 19 | 304 | 40 | 210 | 16 | NA | 600 | 0.3 | 24.29 | 1400000
2023-12-06 | 14700 | 14.7 | 7.49 | 7.9 | 160 | 20 | 296 | 36 | 220 | 12 | NA | 500 | 0.2 | 22.82 | 1700000
2023-12-07 | 15000 | 15 | 7.5 | 7.9 | 155 | 19 | 312 | 36 | 235 | 11 | NA | 400 | 0.2 | 24.53 | 1300000
2023-12-08 | 16410 | 16.41 | 7.38 | 7.93 | 155 | 20 | 296 | 40 | 245 | 10 | NA | 500 | 0.3 | 23.85 | 1400000
2023-12-09 | 15160 | 15.16 | 7.38 | 7.91 | 155 | 18 | 292 | 36 | 230 | 14 | NA | 600 | 0.2 | 23.98 | 1700000
2023-12-10 | 16170 | 16.17 | 7.55 | 7.9 | 155 | 19 | 304 | 40 | 229 | 20 | NA | 500 | 0.2 | 23.5 | 1400000
2023-12-11 | 14100 | 14.1 | 7.55 | 7.92 | 155 | 18 | 300 | 36 | 218 | 22 | NA | 400 | 0.3 | 23.58 | 1300000
2023-12-12 | 14360 | 14.36 | 7.5 | 7.94 | 160 | 19 | 296 | 36 | 225 | 15 | NA | 600 | 0.2 | 23.1 | 1700000
2023-12-13 | 15570 | 15.57 | 7.56 | 7.96 | 160 | 18 | 304 | 40 | 255 | 15 | NA | 500 | 0.2 | 24.07 | 1400000
2023-12-14 | 14690 | 14.69 | 7.65 | 7.85 | 165 | 19 | 288 | 36 | 285 | 18 | NA | 400 | 0.3 | 22.89 | 1300000
2023-12-15 | 15500 | 15.5 | 7.64 | 7.94 | 160 | 18 | 304 | 40 | 260 | 17 | NA | 600 | 0.2 | 23.25 | 1700000
2023-12-16 | 15900 | 15.9 | 7.57 | 7.95 | 155 | 18 | 292 | 36 | 245 | 15 | NA | 400 | 0.3 | 23.62 | 1400000
2023-12-17 | 16430 | 16.43 | 7.52 | 7.94 | 155 | 17 | 288 | 40 | 240 | 18 | NA | 400 | 0.2 | 22.93 | 1700000
2023-12-18 | 15500 | 15.5 | 7.48 | 7.93 | 150 | 18 | 284 | 36 | 242 | 24 | NA | 500 | 0.3 | 23.72 | 1300000
2023-12-19 | 15740 | 15.74 | 7.54 | 7.93 | 155 | 17 | 252 | 28 | 202 | 17 | NA | 600 | 0.2 | 22 | 1700000
2023-12-20 | 16100 | 16.1 | 7.46 | 7.95 | 160 | 18 | 280 | 36 | 250 | 15 | NA | 500 | 0.2 | 23.3 | 1400000
2023-12-21 | 15050 | 15.05 | 7.48 | 7.96 | 165 | 17 | 300 | 40 | 248 | 16 | NA | 600 | 0.3 | 22.25 | 1700000
2023-12-22 | 15010 | 15.01 | 7.45 | 7.96 | 160 | 18 | 296 | 36 | 235 | 18 | NA | 500 | 0.2 | 23.79 | 1400000
2023-12-23 | 14360 | 14.36 | 7.43 | 7.95 | 165 | 19 | 304 | 36 | 270 | 17 | NA | 600 | 0.3 | 22.57 | 1300000
2023-12-24 | 16320 | 16.32 | 7.43 | 7.98 | 160 | 18 | 312 | 40 | 275 | 23 | NA | 400 | 0.2 | 23.29 | 1700000
2023-12-25 | 15330 | 15.33 | 7.45 | 7.95 | 155 | 17 | 288 | 36 | 272 | 24 | NA | 500 | 0.3 | 22.49 | 1300000
2023-12-26 | 15200 | 15.2 | 7.4 | 7.97 | 160 | 18 | 292 | 36 | 260 | 15 | NA | 600 | 0.2 | 23.65 | 1400000
2023-12-27 | 15710 | 15.71 | 7.38 | 7.87 | 155 | 18 | 304 | 40 | 279 | 16 | NA | 400 | 0.3 | 24.17 | 1300000
2023-12-28 | 15110 | 15.11 | 7.45 | 7.79 | 160 | 19 | 316 | 36 | 276 | 17 | NA | 600 | 0.2 | 23.92 | 1700000
2023-12-29 | 19320 | 19.32 | 7.38 | 7.77 | 150 | 18 | 292 | 36 | 279 | 16 | NA | 400 | 0.3 | 22.66 | 1300000
2023-12-30 | 20620 | 20.62 | 7.37 | 7.75 | 155 | 19 | 276 | 40 | 280 | 17 | NA | 600 | 0.2 | 24.2 | 1700000
2023-12-31 | 18160 | 18.16 | 7.34 | 7.74 | 150 | 18 | 280 | 36 | 290 | 17 | NA | 400 | 0.3 | 23.19 | 1300000
Average | 15694.1935 | 15.6942 | 7.4335 | 7.9023 | 157.5806 | 18.4516 | 296.129 | 37.2903 | 248.9355 | 17.9677 |  | 500 | 0.24516 | 23.4632 | 1470967.7419
486.52
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 14000 | 14 | 7.16 | 7.74 | 150 | 17 | 252 | 28 | 202 | 10 |  | 400 | 0.2 | 22 | 1300000
Max | 20620 | 20.62 | 7.65 | 7.98 | 165 | 20 | 316 | 40 | 290 | 28 |  | 600 | 0.3 | 24.53 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 12010 | 12.01 | 7.83 | 7.9 | 160 | 17 | 346 | 40 | 316 | 17 | NA | 400 | 0.3 | 23.82 | 1300000 | From 01.12.2023 to 31.12.2023: 1. Sewage from 13 I&Ds is coming into SPS. 2. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 3. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-12-02 | 10820 | 10.82 | 7.61 | 7.76 | 155 | 14 | 342 | 44 | 314 | 18 | NA | 500 | 0.2 | 23.21 | 1400000
2023-12-03 | 12670 | 12.67 | 7.81 | 7.67 | 160 | 18 | 338 | 42 | 318 | 15 | NA | 400 | 0.3 | 24.49 | 1100000
2023-12-04 | 12960 | 12.96 | 7.63 | 7.74 | 155 | 16 | 340 | 46 | 312 | 13 | NA | 600 | 0.3 | 23.92 | 1300000
2023-12-05 | 12580 | 12.58 | 7.73 | 7.46 | 165 | 19 | 336 | 42 | 317 | 15 | NA | 500 | 0.2 | 24.78 | 1400000
2023-12-06 | 11750 | 11.75 | 7.61 | 7.35 | 160 | 14 | 330 | 44 | 290 | 18 | NA | 400 | 0.2 | 24.67 | 1100000
2023-12-07 | 13910 | 13.91 | 7.58 | 7.32 | 155 | 16 | 336 | 40 | 285 | 16 | NA | 500 | 0.3 | 23.48 | 1300000
2023-12-08 | 12830 | 12.83 | 7.58 | 7.3 | 165 | 18 | 330 | 48 | 280 | 19 | NA | 600 | 0.3 | 24.33 | 1400000
2023-12-09 | 11540 | 11.54 | 7.2 | 6.72 | 155 | 14 | 336 | 42 | 275 | 17 | NA | 400 | 0.2 | 23.85 | 1200000
2023-12-10 | 13010 | 13.01 | 7.47 | 7.21 | 160 | 17 | 338 | 44 | 284 | 15 | NA | 500 | 0.3 | 24.09 | 1100000
2023-12-11 | 11380 | 11.38 | 7.53 | 7.46 | 155 | 18 | 330 | 46 | 280 | 19 | NA | 600 | 0.3 | 23.75 | 1200000
2023-12-12 | 11670 | 11.67 | 7.56 | 7.42 | 165 | 14 | 334 | 42 | 275 | 20 | NA | 400 | 0.2 | 23.55 | 1100000
2023-12-13 | 15220 | 15.22 | 7.61 | 7.53 | 160 | 19 | 332 | 44 | 270 | 22 | NA | 600 | 0.2 | 24.75 | 1400000
2023-12-14 | 16180 | 16.18 | 7.43 | 7.4 | 155 | 22 | 324 | 48 | 274 | 24 | NA | 500 | 0.3 | 24.11 | 1300000
2023-12-15 | 15960 | 15.96 | 7.46 | 7.5 | 160 | 20 | 332 | 40 | 270 | 22 | NA | 400 | 0.3 | 23.78 | 1100000
2023-12-16 | 14390 | 14.39 | 7.41 | 7.51 | 155 | 16 | 328 | 44 | 275 | 26 | NA | 700 | 0.2 | 24.76 | 1400000
2023-12-17 | 14040 | 14.04 | 7.4 | 7.55 | 160 | 18 | 336 | 48 | 278 | 19 | NA | 500 | 0.2 | 24.24 | 1200000
2023-12-18 | 12870 | 12.87 | 7.46 | 7.42 | 155 | 19 | 340 | 44 | 274 | 21 | NA | 400 | 0.3 | 23.82 | 1300000
2023-12-19 | 12420 | 12.42 | 7.08 | 7.18 | 165 | 14 | 336 | 40 | 272 | 20 | NA | 500 | 0.3 | 23.11 | 1100000
2023-12-20 | 12900 | 12.9 | 7.58 | 7.55 | 160 | 18 | 344 | 48 | 280 | 12 | NA | 600 | 0.2 | 24.54 | 1200000
2023-12-21 | 13230 | 13.23 | 7.61 | 7.53 | 155 | 14 | 340 | 44 | 284 | 16 | NA | 400 | 0.2 | 24.07 | 1100000
2023-12-22 | 13260 | 13.26 | 7.56 | 7.49 | 165 | 16 | 336 | 48 | 290 | 12 | NA | 500 | 0.3 | 23.57 | 1300000
2023-12-23 | 13320 | 13.32 | 7.47 | 7.5 | 160 | 19 | 332 | 44 | 288 | 14 | NA | 400 | 0.2 | 23.07 | 1400000
2023-12-24 | 13410 | 13.41 | 7.49 | 7.51 | 165 | 17 | 344 | 36 | 292 | 12 | NA | 600 | 0.3 | 24.69 | 1100000
2023-12-25 | 12240 | 12.24 | 7.71 | 7.41 | 160 | 15 | 340 | 40 | 302 | 16 | NA | 500 | 0.3 | 23.54 | 1200000
2023-12-26 | 13000 | 13 | 7.71 | 7.51 | 155 | 16 | 348 | 44 | 310 | 11 | NA | 400 | 0.3 | 23.94 | 1100000
2023-12-27 | 13700 | 13.7 | 7.54 | 7.44 | 160 | 18 | 344 | 48 | 295 | 14 | NA | 500 | 0.2 | 23.26 | 1200000
2023-12-28 | 12060 | 12.06 | 7.49 | 7.37 | 165 | 14 | 340 | 44 | 280 | 18 | NA | 600 | 0.3 | 24.71 | 1300000
2023-12-29 | 12530 | 12.53 | 7.51 | 7.37 | 160 | 16 | 336 | 40 | 290 | 16 | NA | 400 | 0.3 | 24.1 | 1400000
2023-12-30 | 12790 | 12.79 | 7.63 | 7.39 | 155 | 18 | 340 | 44 | 296 | 12 | NA | 500 | 0.3 | 23.83 | 1300000
2023-12-31 | 13300 | 13.3 | 7.53 | 7.49 | 165 | 19 | 344 | 40 | 280 | 14 | NA | 600 | 0.2 | 24.15 | 1100000
Average | 13030.6452 | 13.0306 | 7.5426 | 7.4503 | 159.5161 | 16.871 | 337.1613 | 43.4839 | 288.5806 | 16.871 |  | 496.7742 | 0.25806 | 23.9994 | 1238709.6774
403.95
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10820 | 10.82 | 7.08 | 6.72 | 155 | 14 | 324 | 36 | 270 | 11 |  | 400 | 0.2 | 23.07 | 1100000
Max | 16180 | 16.18 | 7.83 | 7.9 | 165 | 22 | 348 | 48 | 318 | 26 |  | 700 | 0.3 | 24.78 | 1400000