## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 35990 | 35.99 | 7.58 | 7.76 | 155 | 23 | 296 | 44 | 278 | 34 | NA | 500 | 0.3 | 24.5 | 1100000
2024-02-02 | 36930 | 36.93 | 7.55 | 7.8 | 160 | 21 | 300 | 48 | 266 | 24 | NA | 600 | 0.3 | 24.3 | 1400000
2024-02-03 | 37780 | 37.78 | 7.51 | 7.78 | 165 | 20 | 320 | 44 | 260 | 23 | NA | 400 | 0.2 | 23.88 | 1700000
2024-02-04 | 38580 | 38.58 | 7.49 | 7.73 | 160 | 19 | 312 | 40 | 264 | 24 | NA | 500 | 0.3 | 24.11 | 1200000
2024-02-05 | 47250 | 47.25 | 7.48 | 7.74 | 165 | 20 | 324 | 44 | 287 | 35 | NA | 700 | 0.3 | 24.33 | 1400000
2024-02-06 | 37250 | 37.25 | 7.5 | 7.78 | 160 | 21 | 300 | 48 | 268 | 32 | NA | 400 | 0.3 | 24.17 | 1100000
2024-02-07 | 37240 | 37.24 | 7.52 | 7.8 | 165 | 22 | 320 | 44 | 272 | 38 | NA | 700 | 0.3 | 25.18 | 1200000
2024-02-08 | 35770 | 35.77 | 7.5 | 7.82 | 160 | 23 | 296 | 48 | 267 | 43 | NA | 600 | 0.3 | 24.53 | 1400000
2024-02-09 | 38410 | 38.41 | 7.52 | 7.86 | 165 | 21 | 312 | 44 | 275 | 25 | NA | 400 | 0.2 | 25.3 | 1700000
2024-02-10 | 38430 | 38.43 | 7.48 | 7.82 | 155 | 20 | 300 | 44 | 263 | 27 | NA | 600 | 0.2 | 24.31 | 1200000
2024-02-11 | 40480 | 40.48 | 7.5 | 7.8 | 160 | 21 | 316 | 48 | 266 | 28 | NA | 400 | 0.2 | 25.2 | 1300000
2024-02-12 | 39340 | 39.34 | 7.52 | 7.83 | 170 | 22 | 332 | 44 | 272 | 30 | NA | 500 | 0.3 | 24.47 | 1100000
2024-02-13 | 39310 | 39.31 | 7.5 | 7.81 | 175 | 21 | 328 | 48 | 269 | 32 | NA | 600 | 0.3 | 23.91 | 1400000
2024-02-14 | 48070 | 48.07 | 7.47 | 7.77 | 165 | 22 | 312 | 44 | 281 | 36 | NA | 400 | 0.2 | 24.1 | 1200000
2024-02-15 | 37080 | 37.08 | 7.49 | 7.8 | 160 | 23 | 304 | 48 | 287 | 46 | NA | 700 | 0.2 | 24.17 | 1700000
2024-02-16 | 38580 | 38.58 | 7.48 | 7.79 | 170 | 22 | 312 | 44 | 280 | 42 | NA | 500 | 0.3 | 23.89 | 1100000
2024-02-17 | 37870 | 37.87 | 7.5 | 7.81 | 165 | 23 | 300 | 48 | 283 | 26 | NA | 600 | 0.2 | 24.31 | 1300000
2024-02-18 | 39700 | 39.7 | 7.47 | 7.84 | 170 | 21 | 316 | 44 | 274 | 30 | NA | 400 | 0.2 | 24.37 | 1200000
2024-02-19 | 37690 | 37.69 | 7.48 | 7.83 | 165 | 20 | 304 | 44 | 269 | 42 | NA | 600 | 0.2 | 23.64 | 1400000
2024-02-20 | 37740 | 37.74 | 7.49 | 7.85 | 175 | 21 | 328 | 40 | 275 | 25 | NA | 400 | 0.2 | 24.3 | 1700000
2024-02-21 | 37170 | 37.17 | 7.51 | 7.87 | 165 | 20 | 308 | 36 | 264 | 26 | NA | 500 | 0.3 | 24.11 | 1300000
2024-02-22 | 38640 | 38.64 | 7.53 | 7.86 | 170 | 19 | 328 | 40 | 278 | 29 | NA | 700 | 0.3 | 23.49 | 1100000
2024-02-23 | 39600 | 39.6 | 7.52 | 7.85 | 175 | 18 | 336 | 36 | 263 | 30 | NA | 400 | 0.3 | 24.17 | 1400000
2024-02-24 | 38760 | 38.76 | 7.48 | 7.88 | 180 | 19 | 344 | 40 | 260 | 17 | NA | 500 | 0.3 | 24.1 | 1200000
2024-02-25 | 36870 | 36.87 | 7.5 | 7.89 | 170 | 18 | 328 | 36 | 266 | 19 | NA | 600 | 0.3 | 25 | 1700000
2024-02-26 | 36580 | 36.58 | 7.46 | 7.87 | 160 | 19 | 320 | 40 | 273 | 24 | NA | 400 | 0.2 | 24.33 | 1400000
2024-02-27 | 39800 | 39.8 | 7.41 | 7.85 | 165 | 20 | 324 | 36 | 268 | 32 | NA | 700 | 0.3 | 24.6 | 1100000
2024-02-28 | 39650 | 39.65 | 7.4 | 7.84 | 170 | 19 | 336 | 40 | 275 | 33 | NA | 500 | 0.3 | 25.38 | 1300000
2024-02-29 | 39660 | 39.66 | 7.46 | 7.89 | 160 | 18 | 324 | 36 | 261 | 20 | NA | 400 | 0.2 | 24.15 | 1700000
Average | 38835.1724 | 38.8352 | 7.4931 | 7.8214 | 165.5172 | 20.5517 | 316.5517 | 42.7586 | 271.1724 | 30.069 | NA | 524.1379 | 0.25862 | 24.3552 | 1344827.5862
1126.22
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35770 | 35.77 | 7.4 | 7.73 | 155 | 18 | 296 | 36 | 260 | 17 |  | 400 | 0.2 | 23.49 | 1100000
Max | 48070 | 48.07 | 7.58 | 7.89 | 180 | 23 | 344 | 48 | 287 | 46 |  | 700 | 0.3 | 25.38 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 20590 | 20.59 | 7.35 | 7.76 | 165 | 15 | 308 | 32 | 260 | 38 | NA | 400 | 0.2 | 22.95 | 1300000
2024-02-02 | 18430 | 18.43 | 7.14 | 7.72 | 160 | 18 | 320 | 36 | 295 | 24 | NA | 500 | 0.2 | 22.5 | 1400000
2024-02-03 | 15890 | 15.89 | 7.18 | 7.73 | 160 | 20 | 304 | 40 | 235 | 16 | NA | 600 | 0.3 | 21.46 | 1300000
2024-02-04 | 17950 | 17.95 | 7.39 | 7.74 | 155 | 20 | 284 | 36 | 245 | 20 | NA | 400 | 0.3 | 21.06 | 1400000
2024-02-05 | 22670 | 22.67 | 7.33 | 7.7 | 165 | 19 | 312 | 40 | 370 | 28 | NA | 500 | 0.2 | 22 | 1700000
2024-02-06 | 20570 | 20.57 | 7.52 | 7.72 | 155 | 18 | 284 | 36 | 300 | 18 | NA | 400 | 0.3 | 22.52 | 1300000
2024-02-07 | 18470 | 18.47 | 7.43 | 7.73 | 160 | 15 | 324 | 32 | 290 | 16 | NA | 600 | 0.2 | 23.5 | 1700000
2024-02-08 | 17630 | 17.63 | 7.51 | 7.74 | 165 | 17 | 304 | 32 | 270 | 13 | NA | 500 | 0.2 | 21.33 | 1400000
2024-02-09 | 15400 | 15.4 | 7.53 | 7.75 | 170 | 17 | 316 | 32 | 302 | 12 | NA | 400 | 0.3 | 22.03 | 1300000
2024-02-10 | 13620 | 13.62 | 7.47 | 7.73 | 180 | 16 | 324 | 36 | 304 | 16 | NA | 400 | 0.3 | 23.72 | 1400000
2024-02-11 | 15450 | 15.45 | 7.52 | 7.76 | 165 | 17 | 316 | 32 | 290 | 20 | NA | 600 | 0.2 | 23.26 | 1700000
2024-02-12 | 13500 | 13.5 | 7.58 | 7.77 | 160 | 17 | 312 | 36 | 250 | 19 | NA | 400 | 0.3 | 24 | 1300000
2024-02-13 | 13370 | 13.37 | 7.6 | 7.78 | 155 | 16 | 304 | 40 | 270 | 20 | NA | 600 | 0.2 | 23.54 | 1700000
2024-02-14 | 13850 | 13.85 | 7.52 | 7.76 | 160 | 18 | 312 | 36 | 280 | 19 | NA | 500 | 0.3 | 22.73 | 1400000
2024-02-15 | 13210 | 13.21 | 7.49 | 7.78 | 160 | 19 | 308 | 40 | 270 | 22 | NA | 600 | 0.2 | 22.62 | 1700000
2024-02-16 | 13300 | 13.3 | 7.52 | 7.81 | 165 | 17 | 328 | 40 | 273 | 25 | NA | 500 | 0.2 | 22.29 | 1300000
2024-02-17 | 14100 | 14.1 | 7.45 | 7.85 | 160 | 18 | 316 | 36 | 290 | 26 | NA | 600 | 0.2 | 22.76 | 1700000
2024-02-18 | 13480 | 13.48 | 7.32 | 7.82 | 165 | 18 | 324 | 40 | 280 | 37 | NA | 400 | 0.3 | 23.26 | 1300000
2024-02-19 | 13130 | 13.13 | 7.35 | 7.82 | 165 | 19 | 324 | 36 | 290 | 36 | NA | 600 | 0.2 | 22.95 | 1700000
2024-02-20 | 12880 | 12.88 | 7.27 | 7.81 | 165 | 18 | 332 | 36 | 295 | 26 | NA | 500 | 0.2 | 21.62 | 1400000
2024-02-21 | 13460 | 13.46 | 7.29 | 7.82 | 160 | 17 | 324 | 40 | 300 | 25 | NA | 400 | 0.3 | 23.8 | 1300000
2024-02-22 | 12510 | 12.51 | 7.31 | 7.85 | 165 | 18 | 320 | 36 | 290 | 22 | NA | 600 | 0.2 | 23.28 | 1700000
2024-02-23 | 13610 | 13.61 | 7.3 | 7.84 | 160 | 19 | 248 | 36 | 285 | 27 | NA | 400 | 0.3 | 22.55 | 1300000
2024-02-24 | 13570 | 13.57 | 7.44 | 7.85 | 160 | 18 | 316 | 40 | 290 | 27 | NA | 500 | 0.2 | 24.03 | 1400000
2024-02-25 | 13290 | 13.29 | 7.44 | 7.86 | 165 | 19 | 312 | 36 | 280 | 27 | NA | 600 | 0.3 | 22.73 | 1300000
2024-02-26 | 12990 | 12.99 | 7.41 | 7.84 | 160 | 18 | 308 | 40 | 282 | 29 | NA | 500 | 0.2 | 23.09 | 1700000
2024-02-27 | 12940 | 12.94 | 7.42 | 7.83 | 160 | 18 | 308 | 36 | 290 | 26 | NA | 400 | 0.3 | 22.23 | 1300000
2024-02-28 | 14520 | 14.52 | 7.44 | 7.86 | 155 | 17 | 312 | 40 | 300 | 28 | NA | 500 | 0.3 | 23.35 | 1400000
2024-02-29 | 14720 | 14.72 | 7.42 | 7.86 | 160 | 18 | 312 | 36 | 280 | 29 | NA | 400 | 0.3 | 22.12 | 1300000
Average | 15141.3793 | 15.1414 | 7.4117 | 7.7893 | 162.069 | 17.7241 | 310.8966 | 36.6897 | 284.6897 | 23.8276 |  | 493.1034 | 0.24828 | 22.7338 | 1451724.1379
439.1
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12510 | 12.51 | 7.14 | 7.7 | 155 | 15 | 248 | 32 | 235 | 12 |  | 400 | 0.2 | 21.06 | 1300000
Max | 22670 | 22.67 | 7.6 | 7.86 | 180 | 20 | 332 | 40 | 370 | 38 |  | 600 | 0.3 | 24.03 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 13710 | 13.71 | 7.73 | 7.57 | 160 | 15 | 336 | 40 | 306 | 17 | NA | 600 | 0.3 | 23.56 | 1200000 | From 01.02.2024 to 29.02.2024: 1. Sewage from 13 I&Ds is coming into SPS. 2. Due to cleaning of Chlorine Contact Tank on 17.02.2024 & 18.02.2024, sewage was bypassed before FCR. Hence, parameter testing was not done. 3. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-02-02 | 13990 | 13.99 | 7.79 | 7.58 | 155 | 14 | 340 | 36 | 290 | 12 | NA | 500 | 0.2 | 23.81 | 1400000
2024-02-03 | 13300 | 13.3 | 7.8 | 7.61 | 165 | 16 | 344 | 44 | 295 | 18 | NA | 400 | 0.3 | 24.17 | 1300000
2024-02-04 | 15060 | 15.06 | 7.71 | 7.56 | 160 | 14 | 348 | 40 | 292 | 15 | NA | 600 | 0.3 | 24.35 | 1400000
2024-02-05 | 18990 | 18.99 | 7.75 | 7.54 | 180 | 28 | 412 | 84 | 398 | 62 | NA | 700 | 0.3 | 23.52 | 1700000
2024-02-06 | 14600 | 14.6 | 7.7 | 7.51 | 165 | 22 | 368 | 56 | 346 | 47 | NA | 500 | 0.2 | 23.97 | 1300000
2024-02-07 | 14690 | 14.69 | 7.67 | 7.59 | 160 | 26 | 340 | 70 | 320 | 26 | NA | 400 | 0.3 | 24.16 | 1200000
2024-02-08 | 13300 | 13.3 | 7.61 | 7.57 | 155 | 21 | 344 | 52 | 290 | 31 | NA | 600 | 0.3 | 24.56 | 1100000
2024-02-09 | 14860 | 14.86 | 7.77 | 7.59 | 160 | 18 | 340 | 44 | 296 | 27 | NA | 400 | 0.2 | 23.81 | 1300000
2024-02-10 | 14460 | 14.46 | 7.82 | 7.58 | 155 | 17 | 344 | 40 | 310 | 19 | NA | 500 | 0.2 | 24.05 | 1100000
2024-02-11 | 13770 | 13.77 | 7.75 | 7.55 | 160 | 16 | 348 | 44 | 290 | 20 | NA | 600 | 0.2 | 24.73 | 1400000
2024-02-12 | 14420 | 14.42 | 7.71 | 7.61 | 165 | 15 | 340 | 36 | 286 | 21 | NA | 700 | 0.3 | 23.51 | 1300000
2024-02-13 | 15040 | 15.04 | 7.72 | 7.67 | 155 | 12 | 348 | 40 | 297 | 20 | NA | 500 | 0.2 | 24.17 | 1200000
2024-02-14 | 13720 | 13.72 | 7.74 | 7.68 | 160 | 16 | 336 | 44 | 300 | 18 | NA | 600 | 0.3 | 23.85 | 1100000
2024-02-15 | 13860 | 13.86 | 7.71 | 7.57 | 165 | 14 | 340 | 48 | 296 | 20 | NA | 400 | 0.3 | 23.67 | 1300000
2024-02-16 | 13710 | 13.71 | 7.8 | 7.71 | 160 | 17 | 348 | 44 | 303 | 20 | NA | 500 | 0.2 | 23.13 | 1400000
2024-02-17 | 13770 | 13.77 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-02-18 | 14010 | 14.01 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-02-19 | 14130 | 14.13 | 6.92 | 6.77 | 155 | 11 | 312 | 32 | 320 | 16 | NA | 400 | 0.3 | 24.16 | 1200000
2024-02-20 | 13580 | 13.58 | 7.51 | 7.42 | 160 | 15 | 336 | 44 | 310 | 19 | NA | 600 | 0.3 | 23.75 | 1400000
2024-02-21 | 14680 | 14.68 | 7.79 | 7.64 | 155 | 14 | 340 | 36 | 307 | 17 | NA | 500 | 0.2 | 23.47 | 1300000
2024-02-22 | 14630 | 14.63 | 7.82 | 7.61 | 160 | 15 | 344 | 40 | 312 | 19 | NA | 400 | 0.2 | 24.18 | 1100000
2024-02-23 | 13690 | 13.69 | 7.75 | 7.66 | 165 | 16 | 340 | 44 | 287 | 17 | NA | 600 | 0.3 | 23.82 | 1400000
2024-02-24 | 13290 | 13.29 | 7.82 | 7.64 | 155 | 15 | 344 | 40 | 290 | 20 | NA | 400 | 0.3 | 24.58 | 1300000
2024-02-25 | 14270 | 14.27 | 7.49 | 7.4 | 165 | 16 | 348 | 44 | 306 | 18 | NA | 400 | 0.2 | 23.12 | 1100000
2024-02-26 | 12550 | 12.55 | 7.54 | 7.41 | 160 | 16 | 336 | 40 | 310 | 19 | NA | 600 | 0.3 | 23.78 | 1200000
2024-02-27 | 13640 | 13.64 | 7.71 | 7.58 | 160 | 15 | 340 | 44 | 290 | 17 | NA | 500 | 0.3 | 24.53 | 1400000
2024-02-28 | 12280 | 12.28 | 7.79 | 7.62 | 155 | 14 | 348 | 40 | 286 | 19 | NA | 600 | 0.3 | 24.1 | 1100000
2024-02-29 | 12980 | 12.98 | 7.7 | 7.61 | 165 | 16 | 320 | 44 | 274 | 18 | NA | 400 | 0.3 | 24.11 | 1700000
Average | 14102.7586 | 14.1028 | 7.6896 | 7.55 | 160.5556 | 16.4444 | 343.8519 | 44.8148 | 303.963 | 21.9259 | NA | 514.8148 | 0.26296 | 23.9489 | 1292592.5926
408.98
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12280 | 12.28 | 6.92 | 6.77 | 155 | 11 | 312 | 32 | 274 | 12 |  | 400 | 0.2 | 23.12 | 1100000
Max | 18990 | 18.99 | 7.82 | 7.71 | 180 | 28 | 412 | 84 | 398 | 62 |  | 700 | 0.3 | 24.73 | 1700000