## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 35900 | 35.9 | 7.59 | 7.82 | 155 | 23 | 308 | 40 | 266 | 25 | NA | 500 | 0.2 | 23.92 | 1700000
2024-01-02 | 39600 | 39.6 | 7.49 | 7.78 | 160 | 24 | 312 | 44 | 261 | 23 | NA | 600 | 0.2 | 23.12 | 1400000
2024-01-03 | 43950 | 43.95 | 7.48 | 7.8 | 165 | 23 | 316 | 48 | 270 | 25 | NA | 400 | 0.3 | 24.5 | 1200000
2024-01-04 | 43450 | 43.45 | 7.43 | 7.74 | 155 | 22 | 320 | 44 | 275 | 24 | NA | 500 | 0.2 | 24.11 | 1400000
2024-01-05 | 39600 | 39.6 | 7.48 | 7.81 | 160 | 21 | 312 | 40 | 281 | 21 | NA | 700 | 0.3 | 23.5 | 1100000
2024-01-06 | 39250 | 39.25 | 7.5 | 7.85 | 165 | 22 | 320 | 44 | 288 | 23 | NA | 400 | 0.2 | 24.61 | 1300000
2024-01-07 | 40410 | 40.41 | 7.52 | 7.83 | 160 | 23 | 324 | 40 | 274 | 25 | NA | 600 | 0.2 | 24.86 | 1200000
2024-01-08 | 38370 | 38.37 | 7.55 | 7.85 | 170 | 24 | 328 | 44 | 280 | 24 | NA | 400 | 0.3 | 24.56 | 1400000
2024-01-09 | 36800 | 36.8 | 7.57 | 7.82 | 165 | 23 | 324 | 48 | 272 | 21 | NA | 600 | 0.3 | 25.1 | 1100000
2024-01-10 | 37670 | 37.67 | 7.6 | 7.84 | 170 | 24 | 316 | 44 | 268 | 20 | NA | 500 | 0.3 | 24.55 | 1700000
2024-01-11 | 36380 | 36.38 | 7.61 | 7.83 | 160 | 23 | 324 | 48 | 271 | 20 | NA | 700 | 0.2 | 24.31 | 1300000
2024-01-12 | 37800 | 37.8 | 7.56 | 7.85 | 165 | 24 | 312 | 44 | 277 | 21 | NA | 400 | 0.3 | 25.2 | 1700000
2024-01-13 | 37140 | 37.14 | 7.59 | 7.86 | 160 | 22 | 308 | 40 | 264 | 20 | NA | 500 | 0.3 | 24.37 | 1400000
2024-01-14 | 38200 | 38.2 | 7.57 | 7.81 | 155 | 20 | 300 | 36 | 284 | 21 | NA | 400 | 0.2 | 23.45 | 1700000
2024-01-15 | 39380 | 39.38 | 7.54 | 7.82 | 160 | 21 | 304 | 40 | 270 | 20 | NA | 600 | 0.2 | 24.03 | 1200000
2024-01-16 | 36340 | 36.34 | 7.51 | 7.84 | 155 | 20 | 308 | 36 | 267 | 21 | NA | 500 | 0.3 | 23.87 | 1300000
2024-01-17 | 37060 | 37.06 | 7.52 | 7.79 | 160 | 19 | 300 | 40 | 272 | 25 | NA | 700 | 0.3 | 23.11 | 1100000
2024-01-18 | 36300 | 36.3 | 7.57 | 7.88 | 155 | 20 | 304 | 36 | 275 | 27 | NA | 500 | 0.2 | 22.7 | 1300000
2024-01-19 | 38780 | 38.78 | 7.68 | 7.89 | 160 | 19 | 320 | 40 | 276 | 29 | NA | 400 | 0.3 | 23.95 | 1700000
2024-01-20 | 38710 | 38.71 | 7.61 | 7.84 | 165 | 20 | 312 | 36 | 285 | 25 | NA | 600 | 0.2 | 24.13 | 1400000
2024-01-21 | 39930 | 39.93 | 7.58 | 7.81 | 160 | 21 | 324 | 40 | 274 | 30 | NA | 500 | 0.2 | 24.37 | 1300000
2024-01-22 | 41120 | 41.12 | 7.56 | 7.8 | 155 | 20 | 320 | 44 | 268 | 31 | NA | 700 | 0.3 | 25.1 | 1700000
2024-01-23 | 38290 | 38.29 | 7.6 | 7.79 | 160 | 21 | 328 | 40 | 281 | 32 | NA | 500 | 0.3 | 24.3 | 1100000
2024-01-24 | 36450 | 36.45 | 7.62 | 7.8 | 165 | 22 | 312 | 44 | 266 | 35 | NA | 600 | 0.3 | 24.72 | 1400000
2024-01-25 | 37370 | 37.37 | 7.55 | 7.77 | 160 | 21 | 304 | 40 | 260 | 32 | NA | 400 | 0.3 | 24.4 | 1300000
2024-01-26 | 37920 | 37.92 | 7.57 | 7.74 | 165 | 23 | 312 | 44 | 263 | 37 | NA | 700 | 0.2 | 24.25 | 1200000
2024-01-27 | 38450 | 38.45 | 7.55 | 7.73 | 160 | 22 | 316 | 40 | 266 | 35 | NA | 500 | 0.3 | 25.1 | 1400000
2024-01-28 | 37210 | 37.21 | 7.54 | 7.75 | 165 | 21 | 320 | 44 | 265 | 36 | NA | 400 | 0.2 | 24.13 | 1200000
2024-01-29 | 36970 | 36.97 | 7.52 | 7.74 | 160 | 23 | 328 | 48 | 273 | 40 | NA | 600 | 0.2 | 24.57 | 1100000
2024-01-30 | 37510 | 37.51 | 7.52 | 7.76 | 170 | 24 | 320 | 44 | 270 | 35 | NA | 500 | 0.2 | 23.96 | 1200000
2024-01-31 | 38090 | 38.09 | 7.55 | 7.8 | 160 | 22 | 316 | 48 | 264 | 30 | NA | 700 | 0.3 | 22.53 | 1400000
Average | 38400 | 38.4 | 7.5526 | 7.8077 | 161.2903 | 21.8387 | 315.2258 | 42.1935 | 271.8065 | 26.871 |  | 535.4839 | 0.25161 | 24.1735 | 1351612.9032
1190.4
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35900 | 35.9 | 7.43 | 7.73 | 155 | 19 | 300 | 36 | 260 | 20 |  | 400 | 0.2 | 22.53 | 1100000
Max | 43950 | 43.95 | 7.68 | 7.89 | 170 | 24 | 328 | 48 | 288 | 40 |  | 700 | 0.3 | 25.2 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 16580 | 16.58 | 7.44 | 7.73 | 160 | 19 | 300 | 40 | 300 | 24 | NA | 600 | 0.2 | 23.99 | 1700000
2024-01-02 | 14570 | 14.57 | 7.39 | 7.75 | 165 | 18 | 304 | 40 | 295 | 18 | NA | 400 | 0.3 | 22.65 | 1300000
2024-01-03 | 17820 | 17.82 | 7.35 | 7.73 | 165 | 19 | 328 | 36 | 330 | 30 | NA | 600 | 0.2 | 21.96 | 1700000
2024-01-04 | 14680 | 14.68 | 7.45 | 7.72 | 160 | 18 | 288 | 40 | 260 | 21 | NA | 400 | 0.3 | 22.42 | 1300000
2024-01-05 | 14750 | 14.75 | 7.43 | 7.75 | 165 | 17 | 292 | 32 | 280 | 18 | NA | 500 | 0.2 | 23.47 | 1400000
2024-01-06 | 14230 | 14.23 | 7.49 | 7.76 | 160 | 18 | 304 | 36 | 276 | 19 | NA | 600 | 0.3 | 21.97 | 1300000
2024-01-07 | 14950 | 14.95 | 7.49 | 7.77 | 165 | 17 | 320 | 36 | 285 | 25 | NA | 400 | 0.2 | 21.95 | 1700000
2024-01-08 | 14670 | 14.67 | 7.47 | 7.78 | 160 | 18 | 308 | 32 | 285 | 24 | NA | 600 | 0.2 | 22.22 | 1400000
2024-01-09 | 14980 | 14.98 | 7.51 | 7.77 | 155 | 18 | 312 | 36 | 262 | 20 | NA | 400 | 0.2 | 23.98 | 1300000
2024-01-10 | 14780 | 14.78 | 7.47 | 7.77 | 160 | 19 | 308 | 36 | 265 | 18 | NA | 500 | 0.3 | 21.04 | 1400000
2024-01-11 | 13640 | 13.64 | 7.53 | 7.78 | 155 | 17 | 296 | 32 | 260 | 17 | NA | 400 | 0.3 | 23.09 | 1300000
2024-01-12 | 14290 | 14.29 | 7.53 | 7.79 | 160 | 18 | 312 | 36 | 280 | 19 | NA | 600 | 0.2 | 23.27 | 1700000
2024-01-13 | 15710 | 15.71 | 7.42 | 7.81 | 160 | 17 | 308 | 32 | 275 | 18 | NA | 400 | 0.2 | 21.83 | 1300000
2024-01-14 | 14490 | 14.49 | 7.43 | 7.78 | 165 | 16 | 316 | 36 | 260 | 21 | NA | 400 | 0.3 | 23.21 | 1400000
2024-01-15 | 15530 | 15.53 | 7.65 | 7.78 | 160 | 18 | 284 | 32 | 270 | 25 | NA | 600 | 0.2 | 22.02 | 1700000
2024-01-16 | 14100 | 14.1 | 7.58 | 7.77 | 165 | 16 | 288 | 36 | 265 | 23 | NA | 400 | 0.3 | 23.2 | 1300000
2024-01-17 | 15090 | 15.09 | 7.56 | 7.79 | 160 | 18 | 284 | 32 | 270 | 18 | NA | 500 | 0.3 | 22.79 | 1400000
2024-01-18 | 14870 | 14.87 | 7.45 | 7.82 | 165 | 18 | 308 | 36 | 305 | 21 | NA | 600 | 0.2 | 24.47 | 1700000
2024-01-19 | 14360 | 14.36 | 7.52 | 7.8 | 160 | 16 | 316 | 32 | 280 | 20 | NA | 400 | 0.3 | 23.25 | 1300000
2024-01-20 | 15080 | 15.08 | 7.47 | 7.79 | 165 | 18 | 304 | 36 | 290 | 23 | NA | 500 | 0.2 | 23.39 | 1700000
2024-01-21 | 15320 | 15.32 | 7.45 | 7.8 | 160 | 17 | 312 | 32 | 302 | 24 | NA | 400 | 0.3 | 22.12 | 1400000
2024-01-22 | 16620 | 16.62 | 7.47 | 7.77 | 155 | 18 | 296 | 36 | 290 | 28 | NA | 500 | 0.2 | 22.29 | 1700000
2024-01-23 | 15440 | 15.44 | 7.42 | 7.76 | 155 | 17 | 300 | 32 | 280 | 24 | NA | 400 | 0.3 | 21.22 | 1300000
2024-01-24 | 13100 | 13.1 | 7.51 | 7.81 | 160 | 16 | 304 | 36 | 260 | 17 | NA | 600 | 0.3 | 23.31 | 1400000
2024-01-25 | 13380 | 13.38 | 7.49 | 7.84 | 165 | 17 | 300 | 36 | 270 | 18 | NA | 400 | 0.3 | 21.91 | 1300000
2024-01-26 | 14250 | 14.25 | 7.3 | 7.81 | 160 | 18 | 316 | 32 | 260 | 24 | NA | 500 | 0.3 | 22.42 | 1400000
2024-01-27 | 14500 | 14.5 | 7.42 | 7.79 | 165 | 16 | 304 | 32 | 290 | 28 | NA | 600 | 0.2 | 23.54 | 1700000
2024-01-28 | 13850 | 13.85 | 7.42 | 7.81 | 160 | 18 | 308 | 36 | 290 | 34 | NA | 400 | 0.2 | 23.72 | 1400000
2024-01-29 | 16870 | 16.87 | 7.51 | 7.8 | 165 | 16 | 304 | 36 | 286 | 36 | NA | 600 | 0.2 | 22.35 | 1700000
2024-01-30 | 16200 | 16.2 | 7.42 | 7.82 | 160 | 17 | 300 | 32 | 300 | 34 | NA | 500 | 0.3 | 23.31 | 1400000
2024-01-31 | 20130 | 20.13 | 7.47 | 7.81 | 160 | 16 | 296 | 36 | 280 | 36 | NA | 600 | 0.2 | 21.6 | 1700000
Average | 15123.5484 | 15.1235 | 7.4681 | 7.7826 | 161.129 | 17.3871 | 303.871 | 34.8387 | 280.6774 | 23.3871 |  | 493.5484 | 0.24839 | 22.7084 | 1474193.5484
468.83
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 13100 | 13.1 | 7.3 | 7.72 | 155 | 16 | 284 | 32 | 260 | 17 |  | 400 | 0.2 | 21.04 | 1300000
Max | 20130 | 20.13 | 7.65 | 7.84 | 165 | 19 | 328 | 40 | 330 | 36 |  | 600 | 0.3 | 24.47 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 13940 | 13.94 | 7.59 | 7.5 | 155 | 16 | 340 | 36 | 286 | 18 | NA | 400 | 0.3 | 23.08 | 1200000 | From 01.01.2024 to 05.01.2024: 1. Sewage from 13 I&Ds is coming into SPS. 2. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 3. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-01-02 | 12730 | 12.73 | 7.55 | 7.43 | 165 | 18 | 348 | 44 | 290 | 14 | NA | 600 | 0.3 | 24.12 | 1700000
2024-01-03 | 17500 | 17.5 | 7.71 | 7.41 | 160 | 19 | 344 | 40 | 294 | 17 | NA | 500 | 0.3 | 24.07 | 1300000
2024-01-04 | 13980 | 13.98 | 7.79 | 7.45 | 155 | 18 | 340 | 36 | 285 | 18 | NA | 400 | 0.2 | 23.43 | 1100000
2024-01-05 | 14380 | 14.38 | 7.68 | 7.37 | 165 | 17 | 348 | 44 | 290 | 16 | NA | 500 | 0.2 | 23.7 | 1400000
2024-01-06 | 13630 | 13.63 | 7.53 | 7.49 | 160 | 14 | 340 | 40 | 280 | 18 | NA | 600 | 0.3 | 23.93 | 1300000 | From 06.01.2024 to 31.01.2024: 1. Sewage from 13 I&Ds is coming into SPS. 2. Replacement of trunk sewer between Savitri Nalla & Dham Nalla is complete however, casting for one manhole is incomplete. 3. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-01-07 | 14160 | 14.16 | 7.41 | 7.25 | 155 | 18 | 336 | 40 | 270 | 17 | NA | 400 | 0.2 | 24.91 | 1200000
2024-01-08 | 15330 | 15.33 | 7.6 | 7.47 | 165 | 18 | 340 | 44 | 279 | 14 | NA | 500 | 0.3 | 24.05 | 1100000
2024-01-09 | 14740 | 14.74 | 7.58 | 7.55 | 160 | 15 | 348 | 48 | 282 | 16 | NA | 400 | 0.2 | 24.1 | 1300000
2024-01-10 | 14190 | 14.19 | 7.47 | 7.49 | 155 | 17 | 340 | 44 | 287 | 18 | NA | 600 | 0.3 | 23.53 | 1400000
2024-01-11 | 14630 | 14.63 | 7.44 | 7.37 | 160 | 14 | 344 | 40 | 290 | 15 | NA | 500 | 0.2 | 23.81 | 1100000
2024-01-12 | 13850 | 13.85 | 7.4 | 7.42 | 165 | 16 | 348 | 44 | 304 | 17 | NA | 400 | 0.3 | 24.34 | 1300000
2024-01-13 | 15180 | 15.18 | 7.45 | 7.4 | 160 | 18 | 340 | 36 | 295 | 19 | NA | 600 | 0.2 | 23.72 | 1200000
2024-01-14 | 14130 | 14.13 | 7.79 | 7.46 | 155 | 17 | 336 | 40 | 290 | 16 | NA | 500 | 0.3 | 23.09 | 1400000
2024-01-15 | 14480 | 14.48 | 7.75 | 7.63 | 160 | 14 | 340 | 36 | 285 | 18 | NA | 400 | 0.3 | 24.5 | 1700000
2024-01-16 | 13210 | 13.21 | 7.77 | 7.56 | 155 | 16 | 332 | 40 | 296 | 17 | NA | 500 | 0.2 | 23.23 | 1200000
2024-01-17 | 12970 | 12.97 | 7.7 | 7.57 | 160 | 15 | 336 | 44 | 290 | 14 | NA | 600 | 0.3 | 23.91 | 1100000
2024-01-18 | 13430 | 13.43 | 7.75 | 7.61 | 165 | 18 | 328 | 36 | 310 | 17 | NA | 400 | 0.3 | 24.28 | 1300000
2024-01-19 | 13110 | 13.11 | 7.73 | 7.61 | 160 | 17 | 340 | 44 | 296 | 18 | NA | 500 | 0.2 | 24.05 | 1200000
2024-01-20 | 13240 | 13.24 | 7.79 | 7.59 | 165 | 15 | 336 | 40 | 287 | 17 | NA | 700 | 0.3 | 23.59 | 1400000
2024-01-21 | 13470 | 13.47 | 7.74 | 7.64 | 160 | 16 | 332 | 36 | 290 | 18 | NA | 400 | 0.3 | 23.92 | 1300000
2024-01-22 | 13850 | 13.85 | 7.7 | 7.68 | 155 | 18 | 328 | 32 | 302 | 20 | NA | 500 | 0.2 | 24.3 | 1100000
2024-01-23 | 14530 | 14.53 | 7.61 | 7.49 | 160 | 15 | 336 | 40 | 295 | 16 | NA | 600 | 0.2 | 23.82 | 1200000
2024-01-24 | 14680 | 14.68 | 7.77 | 7.55 | 155 | 19 | 328 | 36 | 308 | 18 | NA | 400 | 0.3 | 24.11 | 1300000
2024-01-25 | 14380 | 14.38 | 7.81 | 7.59 | 160 | 16 | 296 | 40 | 284 | 15 | NA | 500 | 0.3 | 24.52 | 1300000
2024-01-26 | 14500 | 14.5 | 7.75 | 7.57 | 155 | 18 | 332 | 40 | 290 | 18 | NA | 400 | 0.3 | 23.95 | 1400000
2024-01-27 | 13910 | 13.91 | 7.78 | 7.55 | 160 | 16 | 336 | 36 | 297 | 17 | NA | 600 | 0.2 | 23.26 | 1100000
2024-01-28 | 14300 | 14.3 | 7.76 | 7.58 | 165 | 17 | 332 | 44 | 307 | 18 | NA | 500 | 0.2 | 23.56 | 1300000
2024-01-29 | 15170 | 15.17 | 7.8 | 7.6 | 160 | 15 | 340 | 48 | 290 | 17 | NA | 400 | 0.3 | 24.36 | 1400000
2024-01-30 | 15660 | 15.66 | 7.77 | 7.56 | 155 | 18 | 336 | 40 | 306 | 19 | NA | 500 | 0.3 | 23.81 | 1100000
2024-01-31 | 14910 | 14.91 | 7.85 | 7.58 | 160 | 17 | 328 | 36 | 310 | 18 | NA | 400 | 0.2 | 24.05 | 1300000
Average | 14263.5484 | 14.2635 | 7.6716 | 7.5168 | 159.5161 | 16.6129 | 336.3871 | 40.129 | 292.4194 | 17.0323 |  | 490.3226 | 0.25806 | 23.9065 | 1280645.1613
442.17
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12730 | 12.73 | 7.4 | 7.25 | 155 | 14 | 296 | 32 | 270 | 14 |  | 400 | 0.2 | 23.08 | 1100000
Max | 17500 | 17.5 | 7.85 | 7.68 | 165 | 19 | 348 | 48 | 310 | 20 |  | 700 | 0.3 | 24.91 | 1700000