## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 36860 | 36.86 | 7.34 | 7.54 | 160 | 22 | 320 | 44 | 269 | 27 | NA | 600 | 0.2 | 24.5 | 1700000
2023-07-02 | 39020 | 39.02 | 7.3 | 7.78 | 155 | 20 | 312 | 32 | 271 | 23 | NA | 500 | 0.3 | 25.8 | 1200000
2023-07-03 | 44030 | 44.03 | 7.33 | 7.59 | 160 | 15 | 316 | 40 | 267 | 21 | NA | 400 | 0.3 | 24.6 | 1300000
2023-07-04 | 41270 | 41.27 | 7.41 | 7.62 | 170 | 21 | 348 | 36 | 307 | 26 | NA | 800 | 0.3 | 25.3 | 1400000
2023-07-05 | 41230 | 41.23 | 7.36 | 7.7 | 175 | 14 | 332 | 48 | 288 | 21 | NA | 600 | 0.2 | 24.8 | 1200000
2023-07-06 | 47280 | 47.22 | 7.42 | 7.58 | 155 | 19 | 312 | 40 | 295 | 22 | NA | 700 | 0.3 | 25.1 | 1700000
2023-07-07 | 45300 | 45.3 | 7.38 | 7.64 | 165 | 21 | 304 | 36 | 301 | 24 | NA | 500 | 0.3 | 24.3 | 1400000
2023-07-08 | 41590 | 41.59 | 7.32 | 7.66 | 155 | 19 | 308 | 32 | 298 | 23 | NA | 400 | 0.2 | 25.4 | 1700000
2023-07-09 | 46390 | 46.39 | 7.29 | 7.65 | 175 | 21 | 328 | 36 | 284 | 25 | NA | 600 | 0.3 | 25.9 | 1200000
2023-07-10 | 66580 | 66.59 | 7.27 | 7.58 | 170 | 24 | 320 | 44 | 276 | 30 | NA | 800 | 0.3 | 25.1 | 1300000
2023-07-11 | 44440 | 44.45 | 7.24 | 7.7 | 155 | 20 | 316 | 40 | 280 | 25 | NA | 700 | 0.3 | 24.7 | 1400000
2023-07-12 | 41330 | 41.33 | 7.37 | 7.72 | 165 | 22 | 304 | 44 | 278 | 26 | NA | 500 | 0.2 | 25.4 | 1700000
2023-07-13 | 42680 | 42.68 | 7.31 | 7.69 | 155 | 21 | 324 | 48 | 289 | 24 | NA | 400 | 0.3 | 25.8 | 1200000
2023-07-14 | 40590 | 40.59 | 7.36 | 7.72 | 175 | 20 | 328 | 44 | 293 | 22 | NA | 600 | 0.3 | 24.2 | 1100000
2023-07-15 | 41760 | 41.76 | 7.3 | 7.7 | 170 | 22 | 340 | 44 | 277 | 23 | NA | 700 | 0.2 | 24.4 | 1300000
2023-07-16 | 43620 | 43.62 | 7.31 | 7.71 | 175 | 24 | 348 | 48 | 281 | 24 | NA | 500 | 0.2 | 25.4 | 1400000
2023-07-17 | 42730 | 42.73 | 7.35 | 7.68 | 160 | 22 | 320 | 44 | 279 | 26 | NA | 400 | 0.3 | 24.5 | 1700000
2023-07-18 | 42230 | 42.23 | 7.47 | 7.74 | 155 | 21 | 312 | 48 | 302 | 20 | NA | 600 | 0.3 | 26 | 1200000
2023-07-19 | 42970 | 42.97 | 7.69 | 7.64 | 170 | 24 | 324 | 40 | 288 | 21 | NA | 700 | 0.2 | 25.9 | 1300000
2023-07-20 | 40890 | 40.89 | 7.84 | 7.76 | 175 | 23 | 316 | 48 | 297 | 18 | NA | 500 | 0.3 | 24.2 | 1100000
2023-07-21 | 41040 | 41.04 | 7.76 | 7.71 | 160 | 21 | 320 | 40 | 305 | 20 | NA | 600 | 0.3 | 25.8 | 1700000
2023-07-22 | 41700 | 41.7 | 7.74 | 7.68 | 155 | 20 | 308 | 44 | 288 | 15 | NA | 400 | 0.3 | 24.1 | 1400000
2023-07-23 | 44950 | 44.96 | 7.58 | 7.7 | 165 | 23 | 300 | 48 | 293 | 24 | NA | 700 | 0.2 | 24.7 | 1200000
2023-07-24 | 42910 | 42.91 | 7.43 | 7.72 | 155 | 25 | 324 | 44 | 298 | 22 | NA | 500 | 0.2 | 25.9 | 1300000
2023-07-25 | 40790 | 40.79 | 7.68 | 7.74 | 150 | 23 | 312 | 40 | 274 | 20 | NA | 400 | 0.3 | 24.5 | 1100000
2023-07-26 | 43830 | 43.83 | 7.54 | 7.77 | 160 | 27 | 296 | 44 | 267 | 19 | NA | 600 | 0.2 | 25.1 | 1400000
2023-07-27 | 41260 | 41.27 | 7.63 | 7.75 | 150 | 26 | 292 | 40 | 277 | 17 | NA | 500 | 0.3 | 25.7 | 1200000
2023-07-28 | 41020 | 41.02 | 7.68 | 7.72 | 160 | 27 | 320 | 36 | 261 | 18 | NA | 700 | 0.2 | 24.9 | 1700000
2023-07-29 | 52800 | 52.8 | 7.53 | 7.69 | 170 | 26 | 312 | 40 | 258 | 22 | NA | 400 | 0.3 | 26 | 1300000
2023-07-30 | 44970 | 44.37 | 7.59 | 7.78 | 160 | 25 | 300 | 48 | 270 | 21 | NA | 600 | 0.3 | 25.8 | 1400000
2023-07-31 | 62880 | 62.89 | 7.64 | 7.58 | 165 | 23 | 312 | 44 | 281 | 28 | NA | 700 | 0.3 | 25.9 | 1700000
Average | 44223.871 | 44.2042 | 7.4665 | 7.6852 | 162.7419 | 21.9677 | 317.0323 | 42.0645 | 283.6129 | 22.4839 | NA | 567.7419 | 0.26452 | 25.1516 | 1383870.9677
1370.33
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 36860 | 36.86 | 7.24 | 7.54 | 150 | 14 | 292 | 32 | 258 | 15 |  | 400 | 0.2 | 24.1 | 1100000
Max | 66580 | 66.59 | 7.84 | 7.78 | 175 | 27 | 348 | 48 | 307 | 30 |  | 800 | 0.3 | 26 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 15520 | 15.52 | 7.44 | 7.94 | 160 | 16 | 364 | 32 | 315 | 13 | NA | 400 | 0.2 | 22.83 | 1700000
2023-07-02 | 13720 | 13.72 | 7.37 | 7.91 | 165 | 18 | 356 | 28 | 318 | 10 | NA | 600 | 0.3 | 23.51 | 1300000
2023-07-03 | 15230 | 15.23 | 7.43 | 7.87 | 170 | 17 | 368 | 32 | 316 | 11 | NA | 700 | 0.2 | 23.46 | 1400000
2023-07-04 | 16070 | 16.07 | 7.4 | 7.85 | 160 | 20 | 360 | 36 | 315 | 10 | NA | 400 | 0.3 | 23.68 | 1700000
2023-07-05 | 14170 | 14.17 | 7.38 | 7.95 | 165 | 18 | 364 | 32 | 310 | 11 | NA | 700 | 0.2 | 24.58 | 1300000
2023-07-06 | 11210 | 11.21 | 7.46 | 7.8 | 170 | 16 | 368 | 40 | 314 | 12 | NA | 600 | 0.3 | 23.25 | 1400000 | Due to breakage of retaining wall at I&D of Basna Nalla SPS, raw sewage received at Phaphamau STP is less
2023-07-07 | 14820 | 14.82 | 7.4 | 7.93 | 160 | 20 | 360 | 36 | 312 | 10 | NA | 700 | 0.2 | 24.37 | 1700000
2023-07-08 | 15040 | 15.04 | 7.37 | 7.86 | 165 | 17 | 364 | 32 | 310 | 12 | NA | 400 | 0.3 | 23.23 | 1300000
2023-07-09 | 12740 | 12.74 | 7.35 | 7.89 | 155 | 16 | 368 | 28 | 305 | 11 | NA | 700 | 0.2 | 24.91 | 1700000
2023-07-10 | 15280 | 15.28 | 7.4 | 7.94 | 160 | 18 | 360 | 36 | 312 | 13 | NA | 500 | 0.3 | 24.09 | 1400000
2023-07-11 | 12210 | 12.21 | 7.42 | 7.82 | 170 | 15 | 364 | 32 | 310 | 12 | NA | 400 | 0.2 | 22.34 | 1700000
2023-07-12 | 12160 | 12.16 | 7.37 | 7.87 | 165 | 16 | 368 | 44 | 312 | 13 | NA | 700 | 0.3 | 23.97 | 1300000
2023-07-13 | 11810 | 11.81 | 7.43 | 7.9 | 160 | 20 | 364 | 36 | 309 | 10 | NA | 500 | 0.2 | 23.43 | 1700000
2023-07-14 | 12750 | 12.75 | 7.4 | 7.91 | 170 | 14 | 360 | 40 | 314 | 11 | NA | 400 | 0.3 | 23.48 | 1400000
2023-07-15 | 12020 | 12.02 | 7.37 | 7.84 | 160 | 18 | 364 | 32 | 312 | 13 | NA | 500 | 0.2 | 22.97 | 1700000
2023-07-16 | 12720 | 12.72 | 7.41 | 7.91 | 165 | 16 | 368 | 36 | 316 | 10 | NA | 700 | 0.3 | 23 | 1300000
2023-07-17 | 12860 | 12.86 | 7.39 | 7.88 | 160 | 15 | 360 | 28 | 314 | 12 | NA | 600 | 0.2 | 23.79 | 1700000
2023-07-18 | 12170 | 12.17 | 7.4 | 7.94 | 170 | 18 | 364 | 36 | 310 | 14 | NA | 400 | 0.3 | 22.53 | 1300000
2023-07-19 | 12190 | 12.19 | 7.45 | 7.97 | 165 | 16 | 368 | 28 | 313 | 15 | NA | 500 | 0.2 | 23.47 | 1400000
2023-07-20 | 11250 | 11.25 | 7.4 | 7.94 | 160 | 14 | 364 | 36 | 316 | 16 | NA | 600 | 0.3 | 23.03 | 1300000
2023-07-21 | 13060 | 13.06 | 7.42 | 7.93 | 170 | 18 | 354 | 32 | 312 | 13 | NA | 700 | 0.2 | 23.22 | 1700000
2023-07-22 | 11900 | 11.9 | 7.37 | 7.87 | 165 | 17 | 368 | 40 | 314 | 10 | NA | 400 | 0.3 | 23.74 | 1400000
2023-07-23 | 14520 | 14.52 | 7.4 | 7.93 | 160 | 16 | 372 | 44 | 312 | 16 | NA | 600 | 0.2 | 24.18 | 1300000
2023-07-24 | 11550 | 11.55 | 7.42 | 7.9 | 170 | 18 | 360 | 32 | 315 | 14 | NA | 500 | 0.3 | 23.58 | 1400000
2023-07-25 | 11350 | 11.35 | 7.37 | 7.85 | 165 | 20 | 364 | 36 | 313 | 12 | NA | 700 | 0.2 | 24.53 | 1700000
2023-07-26 | 12350 | 12.35 | 7.45 | 7.82 | 160 | 16 | 368 | 40 | 317 | 16 | NA | 400 | 0.3 | 23.95 | 1300000
2023-07-27 | 12920 | 12.92 | 7.35 | 8.75 | 170 | 20 | 360 | 36 | 314 | 13 | NA | 600 | 0.2 | 23.74 | 1700000
2023-07-28 | 13410 | 13.41 | 7.37 | 7.77 | 165 | 22 | 364 | 32 | 318 | 15 | NA | 500 | 0.3 | 22.73 | 1400000
2023-07-29 | 12000 | 12 | 7.4 | 7.78 | 170 | 24 | 368 | 28 | 317 | 12 | NA | 700 | 0.2 | 23.75 | 1300000
2023-07-30 | 13620 | 13.62 | 7.45 | 7.83 | 165 | 23 | 360 | 36 | 318 | 16 | NA | 400 | 0.3 | 24.53 | 1700000
2023-07-31 | 15470 | 15.47 | 7.37 | 7.79 | 170 | 24 | 364 | 40 | 322 | 18 | NA | 500 | 0.2 | 23.71 | 1300000
Average | 13164.1935 | 13.1642 | 7.4003 | 7.9077 | 164.6774 | 17.9355 | 363.8065 | 34.7097 | 313.7097 | 12.7097 | NA | 548.3871 | 0.24839 | 23.5994 | 1480645.1613
408.09
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11210 | 11.21 | 7.35 | 7.77 | 155 | 14 | 354 | 28 | 305 | 10 |  | 400 | 0.2 | 22.34 | 1300000
Max | 16070 | 16.07 | 7.46 | 8.75 | 170 | 24 | 372 | 44 | 322 | 18 |  | 700 | 0.3 | 24.91 | 1700000