## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 35870 | 35.87 | 7.46 | 7.75 | 170 | 22 | 348 | 40 | 316 | 24 | NA | 400 | 0.2 | 25.1 | 1200000
2023-05-02 | 39500 | 39.5 | 7.18 | 7.4 | 160 | 20 | 356 | 36 | 321 | 21 | NA | 500 | 0.3 | 24.5 | 1300000
2023-05-03 | 36150 | 36.16 | 7.5 | 7.82 | 165 | 21 | 336 | 40 | 314 | 20 | NA | 700 | 0.2 | 24.9 | 1200000
2023-05-04 | 43030 | 43.04 | 7.04 | 7.42 | 155 | 20 | 328 | 36 | 317 | 19 | NA | 600 | 0.2 | 23.8 | 1400000
2023-05-05 | 39240 | 39.24 | 7.15 | 7.64 | 160 | 24 | 300 | 44 | 292 | 21 | NA | 400 | 0.3 | 25.3 | 1700000
2023-05-06 | 35010 | 35.02 | 7.23 | 7.57 | 170 | 23 | 316 | 35 | 302 | 24 | NA | 600 | 0.2 | 24.7 | 1400000
2023-05-07 | 35390 | 35.4 | 7.67 | 7.84 | 165 | 25 | 304 | 40 | 273 | 28 | NA | 800 | 0.2 | 25.5 | 1700000
2023-05-08 | 33820 | 33.82 | 7.5 | 7.85 | 160 | 18 | 296 | 36 | 271 | 22 | NA | 400 | 0.3 | 24.4 | 1200000
2023-05-09 | 33960 | 33.96 | 7.66 | 7.46 | 155 | 24 | 320 | 48 | 278 | 32 | NA | 700 | 0.3 | 24.9 | 1700000
2023-05-10 | 33710 | 33.72 | 7.35 | 7.66 | 160 | 26 | 344 | 44 | 321 | 36 | NA | 500 | 0.2 | 25.7 | 1400000
2023-05-11 | 33430 | 33.43 | 7.65 | 7.74 | 170 | 20 | 300 | 40 | 280 | 28 | NA | 400 | 0.2 | 25 | 1200000
2023-05-12 | 33380 | 33.83 | 7.62 | 7.88 | 160 | 16 | 336 | 36 | 284 | 20 | NA | 600 | 0.3 | 24.6 | 1400000
2023-05-13 | 35400 | 35.41 | 7.56 | 7.74 | 165 | 21 | 324 | 32 | 293 | 18 | NA | 400 | 0.2 | 26.1 | 1700000
2023-05-14 | 35180 | 35.18 | 7.33 | 7.66 | 155 | 23 | 352 | 36 | 326 | 17 | NA | 500 | 0.2 | 25.8 | 1200000
2023-05-15 | 34180 | 34.18 | 7.7 | 7.85 | 170 | 18 | 304 | 44 | 282 | 20 | NA | 600 | 0.2 | 26.2 | 1400000
2023-05-16 | 35290 | 35.3 | 7.53 | 7.87 | 160 | 20 | 360 | 40 | 318 | 26 | NA | 400 | 0.3 | 25.2 | 1300000
2023-05-17 | 33700 | 33.7 | 7.57 | 7.86 | 165 | 16 | 328 | 36 | 276 | 22 | NA | 500 | 0.3 | 24.9 | 1700000
2023-05-18 | 34390 | 34.39 | 7.49 | 7.81 | 155 | 19 | 320 | 44 | 292 | 24 | NA | 700 | 0.2 | 25 | 1200000
2023-05-19 | 33620 | 33.63 | 7.53 | 7.84 | 160 | 20 | 312 | 36 | 289 | 25 | NA | 600 | 0.3 | 25.2 | 1400000
2023-05-20 | 34190 | 34.19 | 7.72 | 7.91 | 155 | 22 | 356 | 32 | 323 | 27 | NA | 400 | 0.3 | 25.7 | 1200000
2023-05-21 | 35850 | 35.85 | 7.51 | 7.79 | 165 | 25 | 352 | 44 | 325 | 28 | NA | 700 | 0.2 | 24.9 | 1700000
2023-05-22 | 36480 | 36.48 | 7.46 | 7.76 | 170 | 21 | 320 | 40 | 309 | 24 | NA | 500 | 0.3 | 25.7 | 1400000
2023-05-23 | 33960 | 33.97 | 7.56 | 7.91 | 165 | 20 | 304 | 36 | 281 | 23 | NA | 600 | 0.3 | 26 | 1200000
2023-05-24 | 34050 | 34.05 | 7.68 | 7.94 | 160 | 15 | 320 | 32 | 291 | 16 | NA | 700 | 0.3 | 24.9 | 1700000
2023-05-25 | 36890 | 36.89 | 7.53 | 7.85 | 155 | 18 | 328 | 40 | 301 | 20 | NA | 500 | 0.3 | 23.9 | 1200000
2023-05-26 | 48780 | 48.78 | 7.24 | 7.48 | 160 | 19 | 312 | 48 | 277 | 30 | NA | 800 | 0.2 | 25.5 | 1700000
2023-05-27 | 39860 | 39.87 | 7.28 | 7.56 | 170 | 22 | 332 | 44 | 305 | 27 | NA | 700 | 0.3 | 24.6 | 1400000
2023-05-28 | 39020 | 39.02 | 7.75 | 7.41 | 165 | 24 | 348 | 36 | 312 | 18 | NA | 400 | 0.3 | 26.2 | 1100000
2023-05-29 | 38770 | 38.78 | 7.24 | 7.68 | 155 | 20 | 296 | 32 | 273 | 21 | NA | 600 | 0.3 | 25.1 | 1300000
2023-05-30 | 36900 | 36.9 | 7.68 | 7.81 | 165 | 18 | 320 | 36 | 270 | 19 | NA | 500 | 0.3 | 25.8 | 1200000
2023-05-31 | 36180 | 36.18 | 7.48 | 7.76 | 160 | 20 | 304 | 40 | 293 | 23 | NA | 800 | 0.2 | 24.8 | 1400000
Average | 36296.129 | 36.3142 | 7.479 | 7.7265 | 162.0968 | 20.6452 | 325.0323 | 38.8065 | 296.9355 | 23.3226 | NA | 564.5161 | 0.25484 | 25.1581 | 1393548.3871
1125.74
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33380 | 33.43 | 7.04 | 7.4 | 155 | 15 | 296 | 32 | 270 | 16 |  | 400 | 0.2 | 23.8 | 1100000
Max | 48780 | 48.78 | 7.75 | 7.94 | 170 | 26 | 360 | 48 | 326 | 36 |  | 800 | 0.3 | 26.2 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 14580 | 14.58 | 7.11 | 7.35 | 178 | 16 | 364 | 40 | 322 | 20 | NA | 600 | 0.3 | 24.49 | 1700000
2023-05-02 | 14710 | 14.71 | 7.12 | 7.55 | 170 | 18 | 372 | 36 | 325 | 20 | NA | 500 | 0.2 | 23.52 | 1300000
2023-05-03 | 13500 | 13.5 | 7.17 | 7.76 | 172 | 15 | 368 | 44 | 320 | 21 | NA | 700 | 0.3 | 23.4 | 1400000
2023-05-04 | 17550 | 17.55 | 7.18 | 7.6 | 168 | 16 | 360 | 40 | 318 | 23 | NA | 400 | 0.2 | 24.25 | 1700000
2023-05-05 | 16010 | 16.01 | 7.19 | 7.66 | 162 | 14 | 364 | 36 | 322 | 22 | NA | 500 | 0.3 | 23.2 | 1400000
2023-05-06 | 14340 | 14.34 | 7.1 | 7.65 | 165 | 15 | 368 | 40 | 318 | 16 | NA | 600 | 0.2 | 23.22 | 1300000
2023-05-07 | 13720 | 13.72 | 7.21 | 7.68 | 170 | 18 | 372 | 40 | 321 | 22 | NA | 700 | 0.3 | 24.1 | 1700000
2023-05-08 | 14350 | 14.35 | 7.3 | 7.76 | 165 | 17 | 376 | 36 | 320 | 18 | NA | 400 | 0.2 | 24.9 | 1700000
2023-05-09 | 14780 | 14.78 | 7.32 | 7.79 | 170 | 18 | 368 | 32 | 315 | 21 | NA | 600 | 0.3 | 23.89 | 1400000
2023-05-10 | 13740 | 13.74 | 7.33 | 7.85 | 160 | 15 | 372 | 28 | 328 | 17 | NA | 500 | 0.2 | 23.58 | 1700000
2023-05-11 | 13160 | 13.16 | 7.3 | 7.78 | 172 | 16 | 364 | 36 | 322 | 19 | NA | 700 | 0.3 | 23.01 | 1300000
2023-05-12 | 13150 | 13.15 | 7.31 | 7.69 | 168 | 17 | 368 | 40 | 320 | 18 | NA | 600 | 0.2 | 24.71 | 1700000
2023-05-13 | 14590 | 14.59 | 7.32 | 7.73 | 165 | 18 | 364 | 36 | 327 | 19 | NA | 500 | 0.3 | 23.8 | 1400000
2023-05-14 | 12790 | 12.79 | 7.25 | 7.68 | 173 | 17 | 368 | 40 | 329 | 21 | NA | 700 | 0.2 | 23.32 | 1700000
2023-05-15 | 13260 | 13.26 | 7.3 | 7.65 | 169 | 18 | 372 | 28 | 318 | 18 | NA | 400 | 0.3 | 24.26 | 1300000
2023-05-16 | 14190 | 14.19 | 7.12 | 7.78 | 160 | 15 | 376 | 36 | 315 | 16 | NA | 500 | 0.2 | 23.93 | 1400000
2023-05-17 | 13130 | 13.13 | 7.14 | 7.75 | 162 | 16 | 364 | 32 | 320 | 18 | NA | 400 | 0.3 | 24.17 | 1300000
2023-05-18 | 13310 | 13.31 | 7.15 | 7.65 | 172 | 15 | 368 | 28 | 318 | 17 | NA | 600 | 0.2 | 24.1 | 1700000
2023-05-19 | 14060 | 14.06 | 7.31 | 7.69 | 168 | 16 | 360 | 36 | 326 | 23 | NA | 700 | 0.3 | 23.61 | 1300000
2023-05-20 | 13810 | 13.81 | 7.33 | 7.67 | 165 | 15 | 364 | 40 | 328 | 24 | NA | 500 | 0.2 | 24.69 | 1400000
2023-05-21 | 13100 | 13.1 | 7.31 | 7.68 | 165 | 17 | 372 | 36 | 318 | 18 | NA | 600 | 0.3 | 24.18 | 1300000
2023-05-22 | 13780 | 13.78 | 7.14 | 7.74 | 160 | 15 | 375 | 40 | 322 | 21 | NA | 700 | 0.2 | 23.71 | 1700000
2023-05-23 | 13460 | 13.46 | 7.21 | 7.75 | 165 | 16 | 368 | 32 | 321 | 18 | NA | 500 | 0.3 | 24.25 | 1400000
2023-05-24 | 13070 | 13.07 | 7.23 | 7.78 | 155 | 14 | 364 | 36 | 315 | 14 | NA | 600 | 0.2 | 23.89 | 1300000
2023-05-25 | 12870 | 12.87 | 7.15 | 7.73 | 160 | 18 | 360 | 44 | 322 | 17 | NA | 700 | 0.3 | 24.47 | 1700000
2023-05-26 | 13780 | 13.78 | 7.35 | 7.71 | 170 | 20 | 372 | 36 | 337 | 20 | NA | 500 | 0.2 | 23.27 | 1400000
2023-05-27 | 13860 | 13.86 | 7.21 | 7.75 | 165 | 16 | 368 | 44 | 320 | 23 | NA | 600 | 0.3 | 24.37 | 1300000
2023-05-28 | 13810 | 13.81 | 7.28 | 7.76 | 160 | 18 | 360 | 36 | 324 | 22 | NA | 700 | 0.2 | 23.83 | 1700000
2023-05-29 | 13700 | 13.7 | 7.25 | 7.75 | 155 | 15 | 364 | 40 | 320 | 17 | NA | 400 | 0.3 | 23.97 | 1400000
2023-05-30 | 14100 | 14.1 | 7.24 | 7.78 | 165 | 16 | 368 | 32 | 322 | 18 | NA | 500 | 0.2 | 23.43 | 1700000
2023-05-31 | 13140 | 13.14 | 7.21 | 7.75 | 160 | 14 | 360 | 40 | 319 | 20 | NA | 600 | 0.3 | 24.13 | 1300000
Average | 13916.129 | 13.9161 | 7.2303 | 7.7065 | 165.6129 | 16.2581 | 367.1935 | 36.7742 | 321.6774 | 19.3871 | NA | 564.5161 | 0.25161 | 23.9242 | 1483870.9677
431.4
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12790 | 12.79 | 7.1 | 7.35 | 155 | 14 | 360 | 28 | 315 | 14 |  | 400 | 0.2 | 23.01 | 1300000
Max | 17550 | 17.55 | 7.35 | 7.85 | 178 | 20 | 376 | 44 | 337 | 24 |  | 700 | 0.3 | 24.9 | 1700000