## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 35210 | 35.21 | 7.72 | 7.92 | 175 | 19 | 372 | 36 | 278 | 30 | NA | 500 | 0.3 | 23.77 | 1400000
2024-05-02 | 31650 | 31.65 | 7.68 | 7.94 | 185 | 20 | 384 | 40 | 270 | 26 | NA | 600 | 0.3 | 24.5 | 1100000
2024-05-03 | 37300 | 37.3 | 7.66 | 7.96 | 175 | 18 | 360 | 36 | 287 | 28 | NA | 700 | 0.2 | 24.07 | 1400000
2024-05-04 | 35100 | 35.1 | 7.64 | 7.95 | 180 | 19 | 376 | 32 | 302 | 25 | NA | 400 | 0.3 | 24.13 | 1700000
2024-05-05 | 35350 | 35.35 | 7.65 | 7.97 | 170 | 18 | 356 | 36 | 277 | 26 | NA | 500 | 0.3 | 25.19 | 1400000
2024-05-06 | 35020 | 35.02 | 7.66 | 7.94 | 175 | 17 | 364 | 32 | 289 | 27 | NA | 700 | 0.2 | 24.57 | 1200000
2024-05-07 | 35010 | 35.01 | 7.68 | 7.94 | 180 | 16 | 380 | 32 | 272 | 25 | NA | 600 | 0.2 | 25.12 | 1100000
2024-05-08 | 32920 | 32.92 | 7.6 | 7.91 | 185 | 18 | 384 | 36 | 276 | 26 | NA | 400 | 0.3 | 24.4 | 1700000
2024-05-09 | 35260 | 35.26 | 7.52 | 7.89 | 175 | 20 | 376 | 36 | 286 | 25 | NA | 500 | 0.2 | 24.31 | 1300000
2024-05-10 | 36010 | 36.01 | 7.5 | 7.9 | 180 | 21 | 368 | 40 | 261 | 24 | NA | 600 | 0.2 | 23.11 | 1700000
2024-05-11 | 35060 | 35.06 | 7.45 | 7.88 | 175 | 22 | 372 | 36 | 300 | 27 | NA | 400 | 0.3 | 24.8 | 1100000
2024-05-12 | 31970 | 31.97 | 7.42 | 7.9 | 170 | 21 | 360 | 40 | 283 | 25 | NA | 600 | 0.3 | 23.76 | 1400000
2024-05-13 | 35390 | 35.39 | 7.4 | 7.93 | 180 | 22 | 384 | 36 | 293 | 27 | NA | 700 | 0.3 | 24.18 | 1200000
2024-05-14 | 35450 | 35.45 | 7.38 | 7.91 | 170 | 21 | 356 | 36 | 270 | 24 | NA | 400 | 0.3 | 24.35 | 1400000
2024-05-15 | 35220 | 35.22 | 7.35 | 7.92 | 175 | 20 | 372 | 32 | 283 | 26 | NA | 600 | 0.2 | 23.56 | 1700000
2024-05-16 | 36350 | 36.35 | 7.39 | 7.95 | 170 | 19 | 368 | 36 | 286 | 25 | NA | 700 | 0.2 | 23.81 | 1300000
2024-05-17 | 35790 | 35.79 | 7.48 | 7.94 | 165 | 20 | 348 | 32 | 271 | 26 | NA | 600 | 0.2 | 24.33 | 1100000
2024-05-18 | 35040 | 35.04 | 7.52 | 7.95 | 170 | 19 | 364 | 36 | 302 | 30 | NA | 700 | 0.3 | 23.57 | 1400000
2024-05-19 | 35320 | 35.32 | 7.5 | 7.96 | 160 | 18 | 348 | 32 | 278 | 28 | NA | 500 | 0.2 | 24.44 | 1200000
2024-05-20 | 35340 | 35.34 | 7.48 | 7.97 | 155 | 19 | 344 | 32 | 285 | 27 | NA | 600 | 0.3 | 24.31 | 1700000
2024-05-21 | 35880 | 35.88 | 7.46 | 7.95 | 160 | 18 | 356 | 28 | 290 | 22 | NA | 500 | 0.2 | 23.81 | 1200000
2024-05-22 | 36340 | 36.34 | 7.51 | 7.96 | 165 | 20 | 360 | 32 | 293 | 24 | NA | 400 | 0.2 | 24.22 | 1400000
2024-05-23 | 37680 | 37.68 | 7.61 | 7.98 | 175 | 21 | 380 | 36 | 280 | 25 | NA | 600 | 0.3 | 23.11 | 1700000
2024-05-24 | 36980 | 36.98 | 7.63 | 7.95 | 165 | 20 | 352 | 32 | 278 | 27 | NA | 500 | 0.3 | 24.16 | 1300000
2024-05-25 | 38500 | 38.5 | 7.6 | 7.93 | 160 | 20 | 360 | 36 | 301 | 30 | NA | 700 | 0.3 | 24.41 | 1200000
2024-05-26 | 38580 | 38.58 | 7.65 | 7.95 | 155 | 21 | 348 | 40 | 282 | 29 | NA | 400 | 0.2 | 23.66 | 1700000
2024-05-27 | 35910 | 35.91 | 7.73 | 7.94 | 160 | 20 | 364 | 36 | 274 | 28 | NA | 600 | 0.2 | 24.31 | 1400000
2024-05-28 | 35800 | 35.8 | 7.81 | 7.96 | 155 | 21 | 340 | 40 | 270 | 29 | NA | 700 | 0.2 | 23.77 | 1100000
2024-05-29 | 39320 | 39.32 | 7.8 | 7.98 | 160 | 22 | 320 | 36 | 277 | 30 | NA | 500 | 0.2 | 24.5 | 1300000
2024-05-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | For 30.05.2024 & 31.05.2024: Plant was under shutdown for Reparing work at CCT, Installation of submersible pump in sludge sump and rectification of leakage in header line of MPS.
2024-05-31 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
Average | 33379.0323 | 33.379 | 7.5683 | 7.939 | 169.8276 | 19.6552 | 362.6207 | 35.1724 | 282.5517 | 26.5862 |  | 558.6207 | 0.24828 | 24.1459 | 1372413.7931
1034.75
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.35 | 7.88 | 155 | 16 | 320 | 28 | 261 | 22 |  | 400 | 0.2 | 23.11 | 1100000
Max | 39320 | 39.32 | 7.81 | 7.98 | 185 | 22 | 384 | 40 | 302 | 30 |  | 700 | 0.3 | 25.19 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 16000 | 16 | 7.58 | 7.84 | 175 | 22 | 372 | 44 | 270 | 18 | NA | 500 | 0.3 | 22.3 | 1400000
2024-05-02 | 16200 | 16.2 | 7.49 | 7.84 | 155 | 21 | 304 | 40 | 220 | 17 | NA | 600 | 0.2 | 23.12 | 1700000
2024-05-03 | 15420 | 15.42 | 7.48 | 7.82 | 160 | 22 | 312 | 40 | 270 | 16 | NA | 500 | 0.2 | 23.12 | 1400000
2024-05-04 | 15730 | 15.73 | 7.41 | 7.81 | 180 | 20 | 356 | 44 | 280 | 20 | NA | 600 | 0.2 | 24.09 | 1700000
2024-05-05 | 17320 | 17.32 | 7.5 | 7.85 | 180 | 21 | 344 | 40 | 305 | 24 | NA | 500 | 0.2 | 23.12 | 1400000
2024-05-06 | 17240 | 17.24 | 7.65 | 7.83 | 160 | 21 | 320 | 44 | 300 | 25 | NA | 400 | 0.3 | 23.12 | 1300000
2024-05-07 | 16770 | 16.77 | 7.63 | 7.85 | 165 | 23 | 308 | 40 | 310 | 28 | NA | 600 | 0.2 | 24.12 | 1700000
2024-05-08 | 17790 | 17.79 | 7.64 | 7.84 | 160 | 22 | 312 | 44 | 330 | 27 | NA | 400 | 0.2 | 23.12 | 1400000
2024-05-09 | 17880 | 17.88 | 7.62 | 7.83 | 165 | 21 | 320 | 40 | 310 | 23 | NA | 600 | 0.2 | 24.12 | 1700000
2024-05-10 | 17210 | 17.21 | 7.64 | 7.85 | 165 | 21 | 344 | 40 | 339 | 22 | NA | 500 | 0.2 | 23.59 | 1700000
2024-05-11 | 17820 | 17.82 | 7.61 | 7.82 | 160 | 22 | 324 | 44 | 332 | 26 | NA | 400 | 0.3 | 24.24 | 1300000
2024-05-12 | 16800 | 16.8 | 7.66 | 7.85 | 165 | 21 | 336 | 40 | 348 | 27 | NA | 500 | 0.3 | 23.05 | 1400000
2024-05-13 | 16920 | 16.92 | 7.56 | 7.82 | 160 | 22 | 332 | 44 | 330 | 28 | NA | 600 | 0.2 | 24.12 | 1700000
2024-05-14 | 17190 | 17.19 | 7.46 | 7.86 | 165 | 21 | 320 | 44 | 304 | 23 | NA | 500 | 0.2 | 24.13 | 1400000
2024-05-15 | 17470 | 17.47 | 7.67 | 7.84 | 160 | 22 | 304 | 40 | 278 | 22 | NA | 600 | 0.2 | 23.13 | 1700000
2024-05-16 | 18180 | 18.18 | 7.59 | 7.85 | 160 | 22 | 316 | 40 | 285 | 22 | NA | 400 | 0.3 | 23.12 | 1300000
2024-05-17 | 16050 | 16.05 | 7.71 | 7.87 | 160 | 21 | 304 | 44 | 290 | 24 | NA | 600 | 0.2 | 24.13 | 1700000
2024-05-18 | 16700 | 16.7 | 7.65 | 7.86 | 165 | 22 | 312 | 44 | 235 | 30 | NA | 400 | 0.2 | 24.14 | 1300000
2024-05-19 | 17840 | 17.84 | 7.53 | 7.88 | 170 | 23 | 324 | 40 | 290 | 25 | NA | 400 | 0.2 | 22.14 | 1400000
2024-05-20 | 17030 | 17.03 | 7.44 | 7.85 | 160 | 22 | 304 | 40 | 245 | 21 | NA | 400 | 0.2 | 23.12 | 1300000
2024-05-21 | 17040 | 17.04 | 7.45 | 7.87 | 165 | 23 | 308 | 44 | 244 | 19 | NA | 500 | 0.2 | 24.12 | 1400000
2024-05-22 | 16650 | 16.65 | 7.37 | 7.9 | 160 | 22 | 304 | 44 | 257 | 20 | NA | 600 | 0.2 | 23.16 | 1700000
2024-05-23 | 17840 | 17.84 | 7.5 | 7.88 | 165 | 23 | 316 | 48 | 245 | 21 | NA | 400 | 0.3 | 24.12 | 1300000
2024-05-24 | 17860 | 17.86 | 7.53 | 7.89 | 155 | 22 | 300 | 44 | 252 | 24 | NA | 500 | 0.2 | 24.12 | 1100000
2024-05-25 | 16760 | 16.76 | 7.54 | 7.88 | 160 | 22 | 296 | 48 | 300 | 22 | NA | 600 | 0.2 | 23.91 | 1700000
2024-05-26 | 15900 | 15.9 | 7.59 | 7.87 | 165 | 21 | 320 | 40 | 310 | 21 | NA | 500 | 0.2 | 24.14 | 1400000
2024-05-27 | 16330 | 16.33 | 7.48 | 7.9 | 170 | 19 | 312 | 36 | 305 | 28 | NA | 600 | 0.2 | 24.92 | 1700000
2024-05-28 | 16220 | 16.22 | 7.34 | 7.91 | 160 | 18 | 312 | 40 | 310 | 23 | NA | 500 | 0.2 | 23.19 | 1400000
2024-05-29 | 16360 | 16.36 | 7.29 | 7.92 | 170 | 19 | 324 | 36 | 306 | 22 | NA | 600 | 0.2 | 23.13 | 1700000
2024-05-30 | 16470 | 16.47 | 7.37 | 7.92 | 165 | 20 | 324 | 40 | 325 | 25 | NA | 400 | 0.3 | 22.88 | 1300000
2024-05-31 | 16480 | 16.48 | 7.3 | 7.92 | 165 | 21 | 328 | 40 | 320 | 27 | NA | 500 | 0.3 | 22.91 | 1400000
Average | 16886.129 | 16.8861 | 7.5252 | 7.8619 | 164.1935 | 21.3548 | 319.7419 | 41.8065 | 291.7742 | 23.2258 |  | 506.4516 | 0.22581 | 23.54 | 1483870.9677
523.47
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 15420 | 15.42 | 7.29 | 7.81 | 155 | 18 | 296 | 36 | 220 | 16 |  | 400 | 0.2 | 22.14 | 1100000
Max | 18180 | 18.18 | 7.71 | 7.92 | 180 | 23 | 372 | 48 | 348 | 30 |  | 600 | 0.3 | 24.92 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 10220 | 10.22 | 7.86 | 7.7 | 165 | 15 | 344 | 40 | 290 | 19 | NA | 500 | 0.3 | 23.45 | 1300000 | From 01.05.2024 to 07.05.2024: 1. Sewage from 12 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla is dismantled on 05.04.2024 and sewage is not coming to Shastri Bridge SPS. 3. Due to road widening works, various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-05-02 | 10000 | 10 | 7.75 | 7.59 | 160 | 14 | 340 | 32 | 287 | 18 | NA | 400 | 0.3 | 23.87 | 1200000
2024-05-03 | 10560 | 10.56 | 7.79 | 7.7 | 155 | 13 | 344 | 40 | 285 | 17 | NA | 700 | 0.3 | 24.45 | 1400000
2024-05-04 | 10680 | 10.68 | 7.75 | 7.67 | 160 | 15 | 336 | 44 | 280 | 19 | NA | 600 | 0.3 | 24.08 | 1100000
2024-05-05 | 10620 | 10.62 | 7.86 | 7.69 | 165 | 16 | 348 | 40 | 310 | 20 | NA | 400 | 0.3 | 23.18 | 1400000
2024-05-06 | 10200 | 10.2 | 7.79 | 7.7 | 165 | 15 | 344 | 44 | 302 | 19 | NA | 500 | 0.3 | 24.67 | 1200000
2024-05-07 | 10500 | 10.5 | 7.76 | 7.68 | 160 | 14 | 340 | 36 | 290 | 18 | NA | 600 | 0.3 | 24.29 | 1700000
2024-05-08 | 10770 | 10.77 | 7.77 | 7.69 | 155 | 16 | 348 | 44 | 287 | 17 | NA | 400 | 0.2 | 23.18 | 1100000
2024-05-09 | 10380 | 10.38 | 7.81 | 7.72 | 160 | 15 | 336 | 40 | 310 | 19 | NA | 500 | 0.3 | 23.45 | 1400000 | From 08.05.2024 to 18.05.2024: 1. Sewage from 11 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla is dismantled on 05.04.2024 and sewage is not coming to Shastri Bridge SPS. 3. Due to start of replacement work of trunk sewer after I&D of Bhola Mandir Nalla, sewage from Augharwa nalla is not coming to SPS from 08.05.2024. 4. Due to road widening works, various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 5. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-05-10 | 11400 | 11.4 | 7.86 | 7.68 | 155 | 16 | 332 | 44 | 288 | 17 | NA | 700 | 0.3 | 23.86 | 1200000
2024-05-11 | 11050 | 11.05 | 7.86 | 7.7 | 160 | 15 | 340 | 36 | 293 | 18 | NA | 600 | 0.2 | 24.29 | 1300000
2024-05-12 | 10950 | 10.95 | 7.75 | 7.61 | 165 | 16 | 336 | 44 | 306 | 19 | NA | 400 | 0.3 | 24.62 | 1400000
2024-05-13 | 11350 | 11.35 | 7.82 | 7.68 | 155 | 17 | 344 | 48 | 289 | 17 | NA | 500 | 0.3 | 24.67 | 1300000
2024-05-14 | 10900 | 10.9 | 7.85 | 7.7 | 160 | 16 | 332 | 40 | 310 | 18 | NA | 600 | 0.3 | 23.78 | 1200000
2024-05-15 | 10500 | 10.5 | 7.78 | 7.7 | 165 | 14 | 340 | 44 | 312 | 20 | NA | 400 | 0.3 | 23.19 | 1400000
2024-05-16 | 10620 | 10.62 | 7.86 | 7.73 | 175 | 16 | 356 | 40 | 307 | 21 | NA | 600 | 0.3 | 23.85 | 1700000
2024-05-17 | 10700 | 10.7 | 7.71 | 7.7 | 160 | 15 | 340 | 44 | 297 | 19 | NA | 700 | 0.3 | 24.18 | 1200000
2024-05-18 | 10380 | 10.38 | 7.77 | 7.69 | 165 | 17 | 348 | 48 | 287 | 17 | NA | 400 | 0.2 | 23.8 | 1100000
2024-05-19 | 10450 | 10.45 | 7.88 | 7.7 | 160 | 17 | 344 | 40 | 309 | 19 | NA | 500 | 0.3 | 22.97 | 1400000 | From 19.05.2024 to 23.05.2024: 1. Sewage from 10 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla, Gangoli Shivalay - 1 nalla are dismantled on 05.04.2024, 19.05.2024 respectively and sewage is not coming to Shastri Bridge SPS. 3. Due to start of replacement work of trunk sewer after I&D of Bhola Mandir Nalla, sewage from Augharwa nalla is not coming to SPS from 08.05.2024. 4. Due to road widening works, various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 5. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-05-20 | 10770 | 10.77 | 7.79 | 7.7 | 155 | 16 | 340 | 44 | 288 | 18 | NA | 700 | 0.3 | 24.48 | 1300000
2024-05-21 | 10600 | 10.6 | 7.85 | 7.71 | 165 | 15 | 336 | 40 | 296 | 20 | NA | 600 | 0.2 | 23.68 | 1200000
2024-05-22 | 9850 | 9.85 | 7.81 | 7.68 | 160 | 16 | 340 | 44 | 288 | 17 | NA | 400 | 0.2 | 23.79 | 1700000
2024-05-23 | 10560 | 10.56 | 7.78 | 7.66 | 155 | 15 | 336 | 40 | 297 | 19 | NA | 500 | 0.3 | 23.87 | 1100000
2024-05-24 | 10100 | 10.1 | 7.87 | 7.71 | 160 | 16 | 340 | 44 | 302 | 20 | NA | 700 | 0.2 | 24.16 | 1400000 | From 24.05.2024 to 31.05.2024: 1. Sewage from 9 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla, Gangoli Shivalay - 1 nalla are dismantled on 05.04.2024, 19.05.2024 respectively and sewage is not coming to Shastri Bridge SPS. 3. Due to start of replacement work of trunk sewer after I&D of Bhola Mandir Nalla, sewage from Augharwa nalla is not coming to SPS from 08.05.2024. 4. Due to road widening works, joint between manhole and connecting pipeline from I&D of Dham Nalla is broken, hence sewage from Dham nalla is not coming to SPS from 24.05.2024. 5. Due to road widening works, various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 6. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-05-25 | 9750 | 9.75 | 7.85 | 7.67 | 155 | 16 | 332 | 44 | 288 | 19 | NA | 400 | 0.3 | 24.04 | 1300000
2024-05-26 | 10230 | 10.23 | 7.84 | 7.69 | 165 | 17 | 336 | 48 | 288 | 17 | NA | 600 | 0.3 | 23.55 | 1200000
2024-05-27 | 10040 | 10.04 | 7.73 | 7.63 | 175 | 16 | 356 | 44 | 290 | 18 | NA | 500 | 0.2 | 24.38 | 1700000
2024-05-28 | 10040 | 10.04 | 7.88 | 7.7 | 160 | 15 | 340 | 36 | 310 | 19 | NA | 400 | 0.3 | 23.88 | 1100000
2024-05-29 | 9700 | 9.7 | 7.82 | 7.73 | 180 | 16 | 368 | 40 | 275 | 18 | NA | 600 | 0.3 | 23.68 | 1400000
2024-05-30 | 8750 | 8.75 | 7.74 | 7.64 | 160 | 15 | 336 | 44 | 297 | 20 | NA | 700 | 0.3 | 23.73 | 1300000
2024-05-31 | 9380 | 9.38 | 7.87 | 7.7 | 155 | 16 | 340 | 36 | 302 | 21 | NA | 500 | 0.3 | 24.17 | 1100000
Average | 10387.0968 | 10.3871 | 7.81 | 7.6855 | 161.6129 | 15.5161 | 341.6774 | 41.6774 | 295.4839 | 18.6129 |  | 535.4839 | 0.27742 | 23.911 | 1316129.0323
322
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 8750 | 8.75 | 7.71 | 7.59 | 155 | 13 | 332 | 32 | 275 | 17 |  | 400 | 0.2 | 22.97 | 1100000
Max | 11400 | 11.4 | 7.88 | 7.73 | 180 | 17 | 368 | 48 | 312 | 21 |  | 700 | 0.3 | 24.67 | 1700000